ANL/ESIA-XX/Y

# ETNA Empirical Validation Test Specification

Energy Systems and Infrastructure Analysis Division

About Argonne National Laboratory

Argonne is a U.S. Department of Energy laboratory managed by UChicago Argonne, LLC under contract DE-AC02-06CH11357. The Laboratory’s main facility is outside Chicago, at 9700 South Cass Avenue, Lemont, Illinois 60439. For information about Argonne
and its pioneering science and technology programs, see www.anl.gov.

DOCUMENT AVAILABILITY

Online Access: U.S. Department of Energy (DOE) reports produced after 1991 and a growing 
number of pre-1991 documents are available free at OSTI.GOV (http://www.osti.gov/),
a service of the US Dept. of Energy’s Office of Scientific and Technical Information.

Reports not in digital format may be purchased by the public from the National Technical Information Service (NTIS):

U.S. Department of Commerce

National Technical Information Service

5301 Shawnee Road

Alexandria, VA 22312

www.ntis.gov

Phone: (800) 553-NTIS (6847) or (703) 605-6000

Fax: (703) 605-6900

Email: orders@ntis.gov

Reports not in digital format are available to DOE and DOE contractors from the Office of Scientific and Technical Information (OSTI):

U.S. Department of Energy

Office of Scientific and Technical Information

P.O. Box 62

Oak Ridge, TN 37831-0062

www.osti.gov

Phone: (865) 576-8401

Fax: (865) 576-5728

Email: reports@osti.gov

ANL/ESIA-XX/Y

ETNA Empirical Validation Test Specification

Joel Neymark1, Ralph T. Muehleisen2, Ji-Hyun Kim2, and Timothy McDowell3

1J. Neymark and Associates

2Energy Systems and Infrastructure Analysis Division, Argonne National Laboratory

3Thermal Energy System Specialists

Aug 2023

Contents

Contents	iv

Nomenclature and Abbreviations	ix

1	Introduction	1

1.1	Applicability of Test Method	1

1.2	Organization of Test Cases	1

1.3	Comparing Output to Experimental Results	4

2	Test Procedures	5

2.1	Modeling Approach	5

2.1.1	Time Convention	5

2.1.2	Geometry Convention	5

2.1.3	Non-applicable Inputs	5

2.1.4	Consistent Modeling Methods	5

2.1.5	Equivalent Modeling Methods	6

2.1.6	Use of Non-specified Inputs	6

2.1.7	Simulation Initialization and Preconditioning	6

2.1.8	Simulation Duration	6

2.1.9	Rules for Modifying Simulation Programs or Simulation Inputs	6

2.1.10	(Informative) Recommended Construction Assumptions of this Test Specification	7

2.1.11	(Informative) Simulating HVAC Equipment and Controls	8

2.1.12	Results Submission Requirements	8

2.2	Input Specifications	9

2.2.1	Case ET110A1 Artificial Climate Base Case, Steady-State Overall Building Loss Coefficient with Insulated Windows, Cell A, Applying Specified Catalog Material Properties Except for Selected Imputed Insulation Conductivities	9

2.2.1.1 Informative Note: Objective and Method of the Test Case	9

2.2.1.2 Reserved  (Intentionally blank)	9

2.2.1.3 Test Cell Conditions and Guard Zone Temperatures	10

2.2.1.4 Site Description	11

2.2.1.5 Simulation Duration	12

2.2.1.6 Output Requirements	12

2.2.1.7 Building Geometrical Description, Plans, Characteristics	18

2.2.1.7.1 Geometry	18

2.2.1.7.2 Test Cell Bounding Surface Material Constructions	29

2.2.1.7.3 Surface Radiative Properties	52

2.2.1.7.4 Surface Heat Transfer	53

2.2.1.7.5 Thermal Bridges	54

2.2.1.7.6 Infiltration	54

2.2.1.7.7 Interior Solar Distribution	54

2.2.1.7.8 Internal Gains	54

2.2.1.7.9 Thermal Guards	54

2.2.1.8 Mechanical System	57

2.2.2	Case ET110A2 Artificial Climate Base Case, Steady-State Overall Building Loss Coefficient with Insulated Windows, Cell A, Applying Specified Catalog Material Properties (No Imputed Properties)	59

2.2.2.1 Informative Note: Objective and Method of the Test Case	59

2.2.2.2 Extension Case Basis	59

2.2.2.3 Output Requirements	59

2.2.2.4 Test Cell Bounding Surface Material Constructions	59

2.2.2.5 Infiltration	65

2.2.3	Case ET110B1 Artificial Climate, Steady-State Overall Building Loss Coefficient with Insulated Windows, Cell B, Applying Specified Catalog Material Properties Except for Selected Imputed Insulation Conductivities	66

2.2.3.1 Informative Note: Objective and Method of the Test Case	66

2.2.3.2 Extension Case Basis	66

2.2.3.3 Test Cell Conditions and Guard Zone Temperatures	66

2.2.3.4 Output Requirements	68

2.2.3.5 Geometry	73

2.2.3.6 Test Cell Bounding Surface Material Constructions	78

2.2.3.7 Surface Radiative Properties	85

2.2.3.8 Surface Heat Transfer	85

2.2.3.9 Infiltration	86

2.2.3.10 Internal Gains	86

2.2.3.11 Thermal Guards	87

2.2.3.12 Mechanical System	87

2.2.4	Case ET110B2 Artificial Climate Base Case, Steady-State Overall Building Loss Coefficient with Insulated Windows, Cell B, Applying Specified Catalog Material Properties (No Imputed Properties)	89

2.2.4.1 Informative Note: Objective and Method of the Test Case	89

2.2.4.2 Extension Case Basis	89

2.2.4.3 Output Requirements	89

2.2.4.4 Test Cell Bounding Surface Material Constructions	89

2.2.4.5 Infiltration	90

2.2.5	Case ET100A1 Artificial Climate, Steady-State Overall Building Loss Coefficient with Uninsulated Windows, Cell A, Applying Specified Catalog Material Properties Except for Selected Imputed Insulation Conductivities	91

2.2.5.1 Informative Note: Objective and Method of the Test Case	91

2.2.5.2 Extension Case Basis and Revision Summary	91

2.2.5.3 Test Cell Conditions and Guard Zone Temperatures	91

2.2.5.4 Simulation Duration	92

2.2.5.5 Output Requirments	92

2.2.5.6 Geometry	94

2.2.5.7 Test Cell Bounding Surface Material Constructions	94

2.2.5.7.1 Required Characteristics	94

2.2.5.7.2 Alternative Construction Specification	95

2.2.5.8 Surface Radiative Properties	99

2.2.5.9 Interior Surface Heat Transfer	99

2.2.5.10 Internal Gains	100

2.2.5.11 Thermal Guards	100

2.2.5.12 Mechanical System	100

2.2.6	Case ET100B1 Artificial Climate, Steady-State Overall Building Loss Coefficient with Uninsulated Windows, Cell B, Applying Specified Catalog Material Properties Except for Selected Imputed Insulation Conductivities	101

2.2.6.1 Informative Note: Objective and Method of the Test Case	101

2.2.6.2 Extension Case Basis and Revision Summary	101

2.2.6.3 Test Cell Conditions and Guard Zone Temperatures	101

2.2.6.4 Simulation Duration	102

2.2.6.5 Output Requirments	102

2.2.6.6 Geometry	104

2.2.6.7 Test Cell Bounding Surface Material Constructions	104

2.2.6.7.1 Required Characteristics	104

2.2.6.7.2 Alternative Construction Specification	105

2.2.6.8 Surface Radiative Properties	105

2.2.6.9 Interior Surface Heat Transfer	105

2.2.6.10 Internal Gains	105

2.2.6.11 Thermal Guards	106

2.2.6.12 Mechanical System	106

2.2.7	Case ET100A3 Artificial Climate, Steady-State Overall Building Loss Coefficient with Uninsulated Windows, Cell A, Applying Specified Catalog Material Properties Except for Selected Imputed Insulation Conductivities – with User Selected Interior Surface Heat Transfer Algorithms	107

2.2.7.1 Informative Note: Objective and Method of the Test Case	107

2.2.7.2 Extension Case Basis and Revision Summary	107

2.2.7.3 Output Requirments	107

2.2.7.4 Interior Surface Heat Transfer	110

2.2.7.4.1 Interior Surface Heat Transfer Model	110

2.2.7.4.2 Interior Surface Texture	111

2.2.8	Case ET100B3 Artificial Climate, Steady-State Overall Building Loss Coefficient with Uninsulated Windows, Cell B, Applying Specified Catalog Material Properties Except for Selected Imputed Insulation Conductivities – with User Selected Interior Surface Heat Transfer Algorithms	112

2.2.8.1 Informative Note: Objective and Method of the Test Case	112

2.2.8.2 Extension Case Basis and Revision Summary	112

2.2.8.3 Output Requirments	112

2.2.8.4 Interior Surface Heat Transfer	115

2.2.8.4.1 Interior Surface Heat Transfer Model	115

2.2.8.4.2 Interior Surface Texture	115

2.3	References	116

Nomenclature and Abbreviations

[tk To Do as we get closer to adding test suite to Std 140]

# Introduction

This section gives introductory information about the ETNA empirical validation test procedures. See Section 2 for test specification details.

The ETNA cells are one of the laboratories of the ADEB Branch (Electricity Applications in residential and commercial Buildings) of Electricité De France. This laboratory is called "ETNA" (Essais Thermique en climat Naturel et Artificiel) cells. ETNA could be translated as Thermal Tests in Natural and Artificial Climate. This test specification is based on previous documentation of the experiments (Neymark et al. 2004) and of the test cells (Girault and Guyon 1999).

The configuration of the test facility consists of a building that contains two similarly designed and oriented twin test cells (Cell A and Cell B), with each separated and enclosed by five fixed and separately controlled guard zones. The wall and window facing 30 West of South (nominally “South”) can also be enclosed by a mobile thermal guard; this modular configuration of the south thermal guard zone provides the means for carrying out tests under natural or artificial climatic conditions.

## Applicability of Test Method

This test method applies to building performance simulation (BPS) programs. The purpose of the test method is to evaluate the technical capabilities and range of application of those programs, by comparing simulated results with results from empirical measurements. The experimental test sequences are designed so that the effects of various heat transfer phenomena can be isolated.

## Organization of Test Cases

Cases can be split into 2 sets: ‘artificial climate’ tests and ‘natural climate’ tests.

“Artificial climate” tests are performed, protected from exterior climate by the thermally controlled guards. Temperatures on external walls are imposed on each side of the test cell boundary walls and solar fluxes are assumed to be zero. These cases are numbered “ET1xx”.

For “natural climate” tests, the south guard is removed so that both external temperature and solar energy are natural on the south side. These tests are designed for validation of the simulated behavior of the building under realistic climate conditions. When included, these cases will be numbered “ET2xx”.

This document specifies only the ET100-series artificial-climate steady-state base and extension cases. These cases represent the artificial climate steady-state building loss coefficient (BLC) characterization configuration with and without window insulation, along with surface heat transfer model validation tests, as shown for the eight cases in Table 1. Of these, Case ET110A1 is initially specified, with the remaining cases of Table 1 specified as variations from that or other cases as shown in the table.

Table 1 Steady-State, Artificial-Climate, Test Cases

| Case | Cell | Win. Ins. | k,imp | Interior Surf. h.t. | Base Case | Comments |
| --- | --- | --- | --- | --- | --- | --- |
| ET110A1 | A | Yes | Yes a | h,comb c | -- | Simpler physics: suppressed window h.t.; |
| ET110A2 | A | Yes | No b | h,comb c | ET110A1 | Catalog properties only, unlikely Std 140 case |
| ET100A1 | A | No | Yes a | h,comb c | ET110A1 | Uninsulated window greater heat transfer |
| ET100A3 | A | No | Yes a | Auto d | ET100A1 | Simple context for surface h.t. validation test |
| ET110B1 | B | Yes | Yes a | h,comb c | ET110A1 | Simpler physics: suppressed window h.t. |
| ET110B2 | B | Yes | No b | h,comb c | ET110B1 | Catalog properties only, unlikely Std 140 case |
| ET100B1 | B | No | Yes a | h,comb c | ET110B1 | Uninsulated window greater heat transfer |
| ET100B3 | B | No | Yes a | Auto d | ET100B1 | Simple context for surface h.t. validation test |

- Selected thermal conductivities are imputed based on empirically determined bounding surface UA-values derived from steady-state measured data; other material-property inputs are based on initial catalog-based properties from Girault and Guyon (1999) (or see Neymark et al. [2004]). In these cases infiltration = 0 (is implicit to the imputed conductivities). Imputed thermal conductivities are further discussed in Section 2.1.10.

- Same as “a” except imputed thermal conductivities are replaced by initial catalog data. In these cases infiltration is modeled separately.

- Constant combined interior and exterior surface heat transfer coefficients.

- Automated variation of interior convection and/or radiation heat transfer; algorithms applied within the program are selected by the modeler.

Window insulation is applied in the base case because:

- The natural climate cases include such insulated windows to test sensitivity to solar radiation, where Cell A has an insulated window and Cell B has an uninsulated window, respectively not allowing and allowing transmitted solar radiation.

- In the artificial climate cases, insulated windows are applied in test-cell temperature increase and decay tests related to empirical characterization of thermal mass to drive a greater fraction of heat through boundary surfaces that have greater thermal mass than the windows.

In these test cases, because there is no transmitted solar radiation in the artificial climate configuration, window material layers are specified as opaque materials (i.e., specified to be modeled as walls). This provides a simplified input scheme for:

- checking base-case inputs (mitigate potential for input errors)

- validation testing of 1-D conduction modeling in Cases ET110A1 and ET110B1 (with window insulation) and Cases ET100A1 and B1 (without window insulation)

- validation testing of automated surface heat transfer algorithms in Cases ET100A3 and B3.

Cases ET100A3 and B3 utilize measurements of effective constant combined surface heat transfer coefficients in separate characterization cases that are transposed to these cases. In this steady-state context the user may select any automated surface heat transfer algorithms available in their program for validation within the uncertainty range of the steady-state combined coefficients specified in Cases ET100A1 and B1.

The steady-state artificial-climate cases provide the basis description for all other test cases that will be included in later phases of the project, and they provide the initial configuration for a number of configurations for thermally characterizing each test cell ahead of the broader set of artificial and natural climate empirical validation cases that include a variety of sensitivity test cases.

Sensitivity tests applying only catalog data in the ET110A2 and B2 cases are provided to:

- Indicate the importance of developing imputed conductivities assuming 1D conduction (what most BPS models do) based on measured data versus applying only material properties from catalog data

- Allow modelers to run sensitivity tests to examine causes of the differences between applying imputed conductivities and only catalog values (i.e., filling the gap). Such sensitivities may include evaluating the effects of (e.g.): 2D or 3D conduction, infiltration, surface heat transfer, thermal bridges, heating system radiative/convective split, etc.

Input files should be developed for each test case in the same order as they appear in Table 1.  This allows for the development of a base-case model, with subsequent test-case models developed as modifications to the base case or to cases stemming from the base case. A summary of the experimental sequence underlying the test cases is included in Neymark et al. (2004), Appendix B. The test specification is organized such that Cell A and its guard zones are specified initially; then in later sections Cell B and its guard zones are specified as modifications to Cell A.

Details of each test case are included in Section 2; use this information for setting up simulation inputs. Data needed for running the tests, along with other archived electronic files, are included with the electronic media accompanying the test specification; within this media see “Readme-ET100series-Files.docx” for a guide to its contents. Information regarding the input-data files to use are given in the specifications for each test case.

## Comparing Output to Experimental Results

Output requirements needed for comparison with experimental data differ depending on the case considered. For most test cases, the primary dependent variable for comparison is modeled versus measured overall test cell heating energy. This is accompanied by output of modeled combined convective and radiative heat fluxes at the interior surface of each bounding wall, which are compared with:

q,meas,n = (UA,meas,n x (T,cell – T,guard,n)) / A,n

where:

- q,meas,n is empirically determined steady-state heat flux (W/m2) for each surface (n)

- UA,meas,n is measured UA value (W/K) of each surface (n), isolated in specific characterization cases as described in Appendix C; see “SupplementaryFiles” folder within the accompanying electronic media

- T,cell is measured test cell bulk air temperature, °C

- T,guard,n is temperature of the guard zone (°C) corresponding to each bounding surface (n)

- A,n is surface area (m2) of each bounding surface (n).

There are also a number of other required outputs for input verification. Each test-case specification indicates needed outputs and the name of the file containing empirical data for the case.  Compare simulated required outputs given for each test case to the measured data for the given test case.

For determining whether simulation results agree with empirical data, the user should consider:

- Magnitude of results for individual cases

- Magnitude of difference in results between certain cases (e.g., Case ET100A1 – Case ET110A1)

- Same direction in sensitivity (positive or negative) for difference in results between certain cases (e.g., Case ET100A1 – Case ET110A1).

- Whether results are logically counterintuitive with respect to known or expected physical behavior

- Additional relevant statistical and/or uncertainty analysis.

# Test Procedures

[Note to Modelers: “tk” is used in text to flag minor items needing further editorial attention – e.g., supporting information; numbering of tables, figures, and sections.]

## Modeling Approach

[Note: “Modeling Approach” integrates language consistent with Standard 140-2020, where appropriate.]

### Time Convention

- All references to time in this specification and its accompanying data files are to the local-site time, which is Greenwich Meridian Time + 1 hour (GMT+1).

- This test suite uses the preceding hour time convention, i.e.: Hour 1 = the interval from midnight to 1 A.M; Hour 2 = the interval from 1 A.M. to 2 A.M., etc.

- Do not use daylight savings time.

### Geometry Convention

- If the program being tested includes the thickness of walls in a three-dimensional (3D) definition of the building geometry, then wall, ceiling, and floor thicknesses shall be defined such that the interior air volume of the building model remains as specified. The thicknesses shall extend exterior to the currently defined internal volume. Informative Note: For example, interior air volume of a given test cell would be calculated as 3.500 × 2.565 × 4.655 m = 41.79 m3.

- All test cell and guard zone dimensions provided in this test specification, whether shown from inside or outside the test cell, are interior dimensions unless otherwise indicated.

- All dimensions in meters (m), unless otherwise indicated.

### Non-applicable Inputs

If the specification includes input values that do not apply to the input structure of the program being tested, disregard the nonapplicable inputs and continue. Informative Note: Selected equivalent inputs are included in the test specification for those programs that may need them.

### Consistent Modeling Methods

Where options exist within a simulation program for modeling a specific thermal behavior, consistent modeling methods shall be used for all cases unless specified to be varied for a specific sensitivity case. The option that is used shall be documented in Item M1 of the Pro-Forma Modeler Report; see ModRep_Proforma_ET100series(mmddyy).docx included with the accompanying electronic media. Informative Note: For example, if a program gives a choice of methods for modeling interior surface convection, the same interior surface convection modeling method is to be applied for all cases, except for Cases that specify a different method (e.g., specified methods are different for ET100A3 and B3 versus cases ET100A1, ET100B1, ET110A1, ET110A2, ET110B1, and ET110B2).

### Equivalent Modeling Methods

Where a program or specific model within a program does not allow direct input of specified values, or where input of specified values causes instabilities in a program’s calculations, modelers shall develop equivalent inputs that match the intent of the test specification as nearly as the software being tested allows. Such equivalent inputs shall be developed based on the data provided in the test specification, and such equivalent inputs shall have a mathematical, physical, or logical basis and shall be applied consistently throughout the test cases. The modeler shall document the equivalent modeling method in Item M2 of the Pro-Forma Modeler Report; see ModRep_Proforma_ET100series(mmddyy).docx included with the accompanying electronic media.

### Use of Non-specified Inputs

Non-specified inputs are defined as inputs applied in the program being tested that are not explicitly or sufficiently provided in the test specification.

Use of non-specified inputs shall be permitted only if there is a mathematical, physical, or logical basis for applying them. Where non-specified inputs are used, they shall be applied consistently throughout the test cases. Use of non-specified inputs shall be documented in Item M3 of the Pro-Forma Modeler Report; see ModRep_Proforma_ET100series(mmddyy).docx included with the accompanying electronic media.

### Simulation Initialization and Preconditioning

If the program being tested allows for pre-conditioning (simulation of an initial time period before recording simulation results for the time period of a given test case or series of test cases), use that capability.

Where an input (configuration) change cannot be scheduled, it may be better to use the first few days of data from a given test case for initialization, and compare output only for the last few days or hours of a test case for validation purposes.

### Simulation Duration

Results for each test case shall be taken from the simulation duration time period specified in the appropriate section of this test specification for a given test case. Informative Note: For example, for Case ET110A1, simulation duration is called out in Section 2.2.1.5.

### Rules for Modifying Simulation Programs or Simulation Inputs

2.1.9.1 Modifications to simulation programs or simulation inputs shall have a mathematical, physical, or logical basis and shall be applied consistently across tests. Arbitrary modification of a simulation program’s input or internal code solely for the purpose of more closely matching a given set of results shall be prohibited.

2.1.9.2 If changes are made to the source code of the software for the purpose of performing tests, and these changes are not available in publicly released versions of the software, then the changes shall be documented in sufficient detail, using Item M5 of the pro-forma modeler report template – see ModRep_Proforma_ET100series(mmddyy).docx included with the accompanying electronic media – so that the implications of the changes are assessable.

### (Informative) Recommended Construction Assumptions of this Test Specification

Construction specifications of Section 2.2.1.7.2 are presented as required characteristics and alternative construction specifications.

2.1.10.1 Required characteristics include:

- Empirically determined UA values

- Construction details, as shown in the figures.

2.1.10.2 Alternative construction specifications provided in Section 2.2.1.7.2 consist of material properties tables that include:

- Catalog values

- Imputed thermal conductivities for selected material layers.

2.1.10.2.1 Recommended alternative construction specifications are intended for simulations applying 1-dimensional thermal diffusion models, and are derived based on the interior surface area of a given bounding surface. Informative Appendix C describes calculation of imputed values; see “SupplementaryFiles” folder within the accompanying electronic media.

2.1.10.2.2 Selected thermal conductivities are imputed based on calorimetrically measured UA values, catalog material properties, specified constant interior and exterior combined surface heat transfer coefficients (see Section 2.2.1.7.4), and 1-D conduction analysis developed externally from the tested programs, as described in Appendix C. These imputations are applied because use of nominal catalog values for 1-D heat-transfer modeling based on the interior surface areas of the bounding surfaces results in 30% to 31%[tk] underestimation of overall-building UA value and -12% to 48%[tk] underestimation of individual-wall UA values.

For the more complex test cell bounding surfaces (i.e., floor, ceiling, windows), the test specification assumes the same multiple 1-D parallel path heat flows as applied for the imputed conductivities.

Imputed conductivities are only valid for the given conduction path.

The thermal conductivity imputations implicitly include:

  - Infiltration load

  - 2/3-D edge and corner effects and all as-built thermal bridges

  - 100% convective and 100% efficient heating system

  - Other settings per the test specification of Section 2.

2.1.10.2.3 Justifications for developing alternative construction specifications are to:

- Develop a test specification that conforms with assumptions that can be made by most whole-building performance simulation software.

- Simplify inputs for modelers, so that they can efficiently convey the real as-built experimental facility to their programs in a way that is likely to reduce the potential for interpretation and input errors

- Better emulate thermal mass modeling than with homogeneous blended layers (e.g., if material layers not requiring parallel conduction paths may be needed to test 3-D conduction or other advanced aspects models)

- Convey empirically determined UA-values to model inputs to reduce the potential of unexplainable basis differences in the tested model results versus measured data.

- Apply steady-state calorimetrically determined properties to reduce uncertainty of model results in later dynamic artificial and natural climate cases. These characterizations also mitigate noise in the more dynamic artificial climate and natural climate cases, allowing isolation of causes of later differences to other generally more complex drivers.

The resulting alternative constructions apply imputed thermal conductivities in a way that minimizes interference with how thermal mass would behave if modeled solely based on construction drawings and catalog material properties. The test-cell thermal mass is more important in later non-steady-state dynamic cases. However, the thermal mass is also important in the steady-state cases because it affects the amount of time it takes for the model to reach steady-state, where the initial conditions of the test cell and guard zones for Case ET110A1 are substantially different from the final steady-state conditions.

2.1.10.3  Other modeling options not explicitly specified

Users may develop inputs for other alternative modeling methods according to the instructions of Section 2.1.5 (Equivalent Modeling Methods). For this purpose, the modeler may apply supplementary information about test cell construction provided in Appendix C. Caveats:

a. Appendix C provides more construction detail but there are still unknowns and uncertainties, which is the nature of an empirical-validation specification based on real as-built construction versus ideal synthetic-construction based test specifications of analytical-verification and software-to-software comparative tests.

b. Modelers applying alternative methods should be aware, by including greater input detail or further input simplifications, that they may be increasing the potential for interpretation (and therefore input) errors with respect to their model, and that the test specification developers may not have resources to support assisting with their interpretations.

    - 2.1.11	(Informative) Simulating HVAC Equipment and Controls

The ETNA heating system is designed to emulate an ideal heater (100% efficient, 100% convective, well-mixed air, precise temperature control) intended to measure the building thermal load in a manner that matches assumptions typical of building performance simulation (BPS) software. The selected externally imputed thermal conductivities – based on measured data and evaluated outside of test-intended BPS software – assume an idealized heating system along with other assumptions described in Section 2.1.10.2.2. A separate excursion case may be developed later to compare measured-to-modeled heating energy, where such a case specifies the ETNA heating system in greater detail.

    - 2.1.12	Results Submission Requirements

Upon completion of the test cases herein, the modeler shall provide:

- The required output specified for each test case in Section 2.2

- A completed pro-forma modeler report; see ModRep_Proforma_ET100series(mmddyy).docx included with the accompanying electronic media.

## Input Specifications

The test suite follows the sequence of Table 1; see Section 1.2. Case ET110A1 (see Section 2.2.1) is the artificial climate base case. Later sections describe specific changes to the base case needed for simulating further cases.

### Case ET110A1: Artificial Climate Base Case, Steady-State Overall Building Loss Coefficient with Insulated Windows, Cell A, Applying Specified Catalog Material Properties Except for Selected Imputed Insulation Conductivities

#### Informative Notes: Objective and Method of the Test Case

- For the given test cell properties and experimental data inputs, compare steady-state modeled heater energy to measured heater energy and compare steady-state modeled surface heat flow to measurement-based surface heat flow.

- Guard-zone temperatures were set to approximately Tguards = 10˚C and test cell temperature set to TcellA = 35 ˚C. See data files listed in Section 2.2.1.3 for guard zone and test cell hourly temperatures (set points).

- For an idealized heating system (that effectively outputs building load), apply comparisons during the best steady-state period of the empirical data for the following results:

- Qhtr,model vs Qhtr,measured,avg, where:

  - Qhtr,model ≡ the modeled heating energy consumption output

  - Qhtr,measured,avg ≡ (the average measured heating energy consumption during the given best steady-state period) ± (measurement uncertainty [μ])

- Qsurf,n,model vs Qwall,n,measured, where:

  - Qsurf,n,model ≡ the modeled cumulative convective and radiative heat flow (gain) from the test cell into the given surface at its interior face

  - Qwall,n,measured = UAsurface,n,measured x (Tcell – Tguard,n), where

    - UAsurface,n,measured ≡ measured UA value from the test specification; also see Appendix C (see “SupplementaryFiles” folder within the accompanying electronic media), Table 3 (for Cell A) or Table 4 (for Cell B)

    - Tcell ≡ measured test cell temperature

    - Tguard,n ≡ measured temperature of the guard zone corresponding to the given surface

  - Individual surface and/or heat flow path (or selected aggregated paths) comparisons allow isolation of differences for given walls or heat flow paths.

#### Reserved

#### Test Cell Conditions and Guard-zone Temperatures

##### Test Cell Measured Data and Weather Input Data

Hourly data files and the test data sets durations for Case ET110A1 are listed in Table 2. These data files are included with the accompanying electronic media; also see Readme-ET100series-Files.docx there. The following conventions apply to the data files:

- Preceding-hour time convention: e.g., the data corresponding to time 2:00 (hour 2) is the data averaged during the preceding hour period from 1:00 to 2:00.

- The time zone reference for the data is GMT+1.

Table 2 Primary Data File Directory

| File Name | Data Type | Time Step | Data Duration (“MM/DD/YYYY hh”) |
| --- | --- | --- | --- |
| ET110A-Measurements-GMT+1.csv c | Test Cell A | Hour | 01/26/2000 12 through 02/11/2000 09 |
| ET110meteoGMT+1_within_Melun-071530_MY.2000.epw a,b,c | Local ETNA weather inserted within Melun, France AMY data | Hour | 01/01/2000 01 through 12/31/2000 24 |

a. Informative Note: Epw format is described at: http://climate.onebuilding.org/papers/EnergyPlus_Weather_File_Format.pdf.

b. Informative Note: In the artificial climate cases, for programs that model guard zones as boundary conditions applied to each test cell wall rather than as literal zones, the weather data is essentially dummy data – i.e., not used in the model other than to satisfy the requirement of most BPS software to have a weather data set.

c. Informative Note: For further supporting information regarding these data files, see Readme-ET100series-Files.docx and also Neymark et al. (2004), Appendix A.

The ET110A-Measurements-GMT+1-mmddyy.csv hourly data format is given in Table 3. The header labels of Table 3 apply as follows:

- “Column” identifies the column where the data appears as viewed with Microsoft ExcelTM

- “Label” is the data descriptor provided in Row 3 of the csv file

- “Usage” is the data purpose provided in Row 1 of the csv file, where data marked:

  - “Input” shall be applied as input to the software being tested

  - “Output” (only for data labeled “Qhtr”) shall be applied for comparison with the Qhtr output of the software being tested; see Section 2.2.1.6 regarding software output requirements, and Section 2.2.1.6.3 regarding comparison of software results to empirical data

- “Description” is a brief description of the measured data

- “Units” are the SI units of the measured data in Row 4 of the csv file.

Table 3 Cell A Hourly Data Format

| Column | Label | Usage | Description | Units |
| --- | --- | --- | --- | --- |
| A | Date | Input | Date and time in format “MM/DD/YYYY hh:mm” (preceding hour format, e.g., Hour 10:00 = 09:00-10:00) |  |
| B | Tattic | Input | Attic air temperature a | ºC |
| C | Tcellar | Input | Cellar air temperature a | ºC |
| D | Tnorth | Input | North guard air temperature a | ºC |
| E | Teast | Input | East guard air temperature a | ºC |
| F | Tsouth | Input | South guard air temperature a | ºC |
| G | Twest | Input | West guard air temperature a | ºC |
| H | Tcell | Input | Test cell setpoint temperature a | ºC |
| I | Qfan | Input | Fan energy | Wh |
| J | HWDsafr | Input | Fan supply airflow rate | m3/h |
| K | Qhtr | Output | Heater energy | Wh |

a. See Figure 1 (Section 2.2.1.7.1.1) for location of zones.

Informative Notes:

- Within the .csv file each line contains data for one hour, and the first four lines include column labels and units.

- Cell A air (setpoint) temperature sensor locations are given in Neymark et al. (2004), Figure 18 (Section 2.2.1.7.2). Guard zone temperature sensors were located centrally to represent average guard zone temperatures; the precise locations were not documented.

##### Informative Note: Input Data Checking for All Test Cases

Original test cell and and local ETNA weather data were checked and corrected as described in Neymark et al. (2004), Appendix A, Section A.2. Subsequent data checking is documented with informative accompanying files; see Readme-ET100series-Files.docx, included with the accompanying electronic media.

#### Site Description

Location and site data for the ETNA cells is provided in Table 4. The facility is in a rural environment, without any obstacle (detached shading) on the South façade over a length of 100 meters.

Table 4 ETNA Geographic Situation

| Latitude | 48°22’ N |
| --- | --- |
| Longitude | 2° 49’ E |
| Altitude | 104 m |
| Localization | Country, open terrain with scattered obstructions a |
| Soil reflectivity (estimation) | 0.2 |
| Orientation | “South wall” faces 30° West of South (see Figure 1, Section 2.2.1.7.1.1) |

a. Informative Note: Site localization corresponds with Terrain Category 3, documented in 2021 ASHRAE Handbook-Fundamentals, p. 24.4, Table 1

#### Simulation Duration

Time period of simulation: 01/26/2000 12:00 through 02/11/2000 09:00 (GMT+1); time period convention is MM/DD/YYYY hh:mm.

This is the same time period as the ET110A-Measurements-GMT+1.csv input file; see Section 2.2.1.3.1.

#### Output Requirements

Provide output applying tab ET110A1 of the template ET100series-output-GMT+1….xlsx, included with the accompanying electronic media. The following requirements shall apply:

- Table 5 lists required and optional hourly-integrated-average outputs

- Output shall be provided for the simulation duration time period indicated in Section 2.2.1.5.

- Output shall apply the preceding-hour time convention of Section 2.1.1.

  - This shall be documented in Item G10 of the pro-forma modeler report; see ModRep_Proforma_ET100series(mmddyy).docx included with the accompanying electronic media.

  - If the program being tested cannot provide output applying preceding-hour time convention, the user shall indicate the tested program output convention in Item G10 of their pro-forma modeler report.

- Do not make changes to the output template. Informative Note: The template is set up for automated data handling; any changes to it will disrupt that process.

2.2.1.6.1 Inside Surface Flux Output

For software applying the 16 alternative 1-D conduction paths specified in Section 2.2.1.7.2.1.2 and related subsections of Section 2.2.1.7.2, this output (see Table 5) shall be provided as allowed by the software being tested. This output corresponds with each 1-D conduction path specified in Section 2.2.1.7.2. Informative Note: This diagnostic output is provided to check modeling of individual 1-D conduction paths.

2.2.1.6.1.1 Inside surface convective flux (Wh/m2). This is the convective flux (gain) from the test cell into the given surface at its interior face. A positive value indicates heat is flowing from the test cell into the surface.

2.2.1.6.1.2 Inside surface radiative flux (Wh/m2). This is the radiative flux (gain) from the test cell into the given surface at its interior face. A positive value indicates heat is flowing from the test cell into the surface.

2.2.1.6.1.3 Inside surface combined convective and radiative flux (Wh/m2). This is the sum of the convective and radiative fluxes; see Sections 2.2.1.6.1.1 and 2.2.1.6.1.2, respectively.

##### 2.2.1.6.2  Output Format

Table 5 also describes format of the output template.  Date and hour data described for worksheet column A is already provided in the template. Data for the other columns shall be provided for the program being tested. The following apply:

- Time zone is GMT+1

- Date is same as for the input data

- Informative Note: Reporting of test cell and guard zone air temperatures and fan energy are intended as input checks; the primary dependent variable is heating energy consumption (Qhtr).

The header labels of Table 5 apply as follows:

- “Column” identifies the column where the data appears as viewed with Microsoft ExcelTM

- “Label” is the data descriptor provided in Row 4 of the output template

- “Usage” is the output purpose provided in Row 1 of the output template, where data marked:

  - “Input Check” data shall be applied for checking “input” data to the software being tested (see Section 2.2.1.3.1)

  - “Required Output” (only for data labeled “Qhtr”) shall be applied for comparison with the provided “output” measured heating energy (see Section 2.2.1.3.1)

  - “Optional Output” shall be allowed for comparison with the provided measurement-based individual surface heat flow output (see Section 2.2.1.6.3) , for software applying the 16 alternative 1-D conduction paths specified for this test case.

    - Informative Note: This output may be provided if the software being tested allows this output or a subset of this output.

- “Description” is a brief description of the listed output; see Row 3 of the output template

- “Units” are the SI units of the measured data in Row 5 of the output template.

Output file names shall indicate the simulation tool and submission date (yyyymmdd). For example, a “Software A ‘(A)’” results file for Case ET110A1 submitted Oct 15, 2023 may be named “A-ET100series-20230915”.

- Table 5.  Cell A Hourly Output File Format

| Column | Label | Usage | Description | Units |
| --- | --- | --- | --- | --- |
| A | Date | Input Check | Date and time in format “MM-DD-YYYY hh:mm” (preceding hour format, e.g., Hour 10:00 = 09:00-10:00) |  |
| B | Tattic | Input Check | Attic air temperature | ºC |
| C | Tcellar | Input Check | Cellar air temperature | ºC |
| D | Tnorth | Input Check | North guard air temperature | ºC |
| E | Teast | Input Check | East guard air temperature | ºC |
| F | Tsouth | Input Check | South guard air temperature | ºC |
| G | Twest | Input Check | West guard air temperature | ºC |
| H | Tcell | Input Check | Test cell air temperature | ºC |
| I | Qfan | Input Check | Fan energy consumption | Wh |
| J | HWDsafr | Input Check | Supply air flow rate | m3/h |
| K | Qhtr | Required Output | Heater energy consumption | Wh |
| L | q,c1,conv | Optional Output | Ceiling Path 1 inside surface convective flux a | Wh/m2 |
| M | q,c1,rad | Optional Output | Ceiling Path 1 inside surface radiative flux a | Wh/m2 |
| N | q,c1,tot | Optional Output | Ceiling Path 1 inside surface total convective and radiative flux a | Wh/m2 |
| O | q,c2,conv | Optional Output | Ceiling Path 2 inside surface convective flux a | Wh/m2 |
| P | q,c2,rad | Optional Output | Ceiling Path 2 inside surface radiative flux a | Wh/m2 |
| Q | q,c2,tot | Optional Output | Ceiling Path 2 inside surface total convective and radiative flux a | Wh/m2 |
| R | q,f1,conv | Optional Output | Floor Path 1 inside surface convective flux a | Wh/m2 |
| S | q,f1,rad | Optional Output | Floor Path 1 inside surface radiative flux a | Wh/m2 |
| T | q,f1,tot | Optional Output | Floor Path 1 inside surface total convective and radiative flux a | Wh/m2 |
| U | q,f2,conv | Optional Output | Floor Path 2 inside surface convective flux a | Wh/m2 |
| V | q,f2,rad | Optional Output | Floor Path 2 inside surface radiative flux a | Wh/m2 |
| W | q,f2,tot | Optional Output | Floor Path 2 inside surface total convective and radiative flux a | Wh/m2 |
| X | q,f3,conv | Optional Output | Floor Path 3 inside surface convective flux a | Wh/m2 |
| Y | q,f3,rad | Optional Output | Floor Path 3 inside surface radiative flux a | Wh/m2 |
| Z | q,f3,tot | Optional Output | Floor Path 3 inside surface total convective and radiative flux a | Wh/m2 |
| AA | q,n,conv | Optional Output | North wall inside surface convective flux a | Wh/m2 |
| AB | q,n,rad | Optional Output | North wall inside surface radiative flux a | Wh/m2 |
| AC | q,n,tot | Optional Output | North wall inside surface total convective and radiative flux a | Wh/m2 |
| AD | q,d,conv | Optional Output | Door inside surface convective flux a | Wh/m2 |
| AE | q,d,rad | Optional Output | Door inside surface radiative flux a | Wh/m2 |
| AF | q,d,tot | Optional Output | Door inside surface total convective and radiative flux a | Wh/m2 |
| AG | q,e,conv | Optional Output | East wall inside surface convective flux a | Wh/m2 |
| AH | q,e,rad | Optional Output | East wall inside surface radiative flux a | Wh/m2 |
| AI | q,e,tot | Optional Output | East wall inside surface total convective and radiative flux a | Wh/m2 |
| AJ | q,ewin1,conv | Optional Output | East window Path 1 inside surface convective flux a | Wh/m2 |
| AK | q,ewin1,rad | Optional Output | East window Path 1 inside surface radiative flux a | Wh/m2 |
| AL | q,ewin1,tot | Optional Output | East window Path 1 surface total convective & radiative flux a | Wh/m2 |
| AM | q,ewin2,conv | Optional Output | East window Path 2 inside surface convective flux a | Wh/m2 |
| AN | q,ewin2,rad | Optional Output | East window Path 2 inside surface radiative flux a | Wh/m2 |
| AO | q,ewin2,tot | Optional Output | East window Path 2 surface total convective and radiative flux a | Wh/m2 |
| AP | q,ewin3,conv | Optional Output | East window Path 3 inside surface convective flux a | Wh/m2 |
| AQ | q,ewin3,rad | Optional Output | East window Path 3 inside surface radiative flux a | Wh/m2 |
| AR | q,ewin3,tot | Optional Output | East window Path 3 surface total convective and radiative flux a | Wh/m2 |
| AS | q,s,conv | Optional Output | South wall inside surface convective flux a | Wh/m2 |
| AT | q,s,rad | Optional Output | South wall inside surface radiative flux a | Wh/m2 |
| AU | q,s,tot | Optional Output | South wall inside surface total convective and radiative flux a | Wh/m2 |
| AV | q,swin1,conv | Optional Output | South window Path 1 inside surface convective flux a | Wh/m2 |
| AW | q,swin1,rad | Optional Output | South window Path 1 inside surface radiative flux a | Wh/m2 |
| AX | q,swin1,tot | Optional Output | South window Path 1 surface total convective & radiative flux a | Wh/m2 |
| AY | q,swin2,conv | Optional Output | South window Path 2 inside surface convective flux a | Wh/m2 |
| AZ | q,swin2,rad | Optional Output | South window Path 2 inside surface radiative flux a | Wh/m2 |
| BA | q,swin2,tot | Optional Output | South window Path 2 surface total convective and radiative flux a | Wh/m2 |
| BB | q,swin3,conv | Optional Output | South window Path 3 inside surface convective flux a | Wh/m2 |
| BC | q,swin3,rad | Optional Output | South window Path 3 inside surface radiative flux a | Wh/m2 |
| BD | q,swin3,tot | Optional Output | South window Path 3 surface total convective and radiative flux a | Wh/m2 |
| BE | q,w,conv | Optional Output | West wall inside surface convective flux a | Wh/m2 |
| BF | q,w,rad | Optional Output | West wall inside surface radiative flux a | Wh/m2 |
| BG | q,w,tot | Optional Output | West wall inside surface total convective and radiative flux a | Wh/m2 |

a. See Section 2.2.1.6.1.

##### 2.2.1.6.3  Comparing Software Output to Measured Data and Empirical Values Derived from Measured Data

Results comparisons shall be applied only for the given best steady-state period of the data; see Section 2.2.1.6.3.1.

The following measured data are provided for results comparisons for all models:

- Heater energy (Qhtr): see Section 2.2.1.6.3.2

The following empirical values derived from measured data are provided for software applying the 16 alternative 1-D conduction paths specified for this test case:

- Total surface heat fluxes (q,x,tot) for each conduction path (x): see Section 2.2.1.6.3.3

Informative Note (for Simulation Trials): The ETNA project team will be compiling all submitted results and presenting results sets anonymously until all simulation trial participants have provided permission to publish results that identify participating software. However, it is recommended to compare results and fix input errors (if any are identified) ahead of submitting initial results. If input errors are found, and may be related to test specification ambiguities, include discussion of the issue in the provided pro-forma modeler report; see Item M7 of ModRep_ProForma_ET100Series(mmddyy).docx with the accompanying electronic media. Similarly, if software errors are found and fixed, also document that in Item M7 of the pro-forma modeler report.

2.2.1.6.3.1 Application of Best Steady-State Data

For Case ET110A1, the best steady-state time period is:

2/10/2000 16:00 to 2/11/2000 9:00, GMT+1

(The time interval applies “MM/DD/YYYY hh:mm” format and preceding hour interval time convention of Section 2.1.1)

Informative Note: Determination of the best steady-state period for a given test case is described in Appendix C; see “SupplementaryFiles” folder within the accompanying electronic media.

2.2.1.6.3.2 Comparison of Required Heater Energy (Qhtr) Results

The primary results comparison is for Qhtr provided in ET110A-Measurements-GMT+1.csv (see Section 2.2.1.3.1), corresponding with the best steady-state period (last 18 rows of the csv file).

Informative Note: If the program has input the test case correctly, for steady-state output it is reasonable to expect modeled hourly output Qhtr during the best steady-state period that is mostly within averaged measured Qhtr ± u(Q), Here, u(Q) is ± 1.4%[tk] for a 2-sigma (95% confidence interval) uncertainty band.

2.2.1.6.3.3 Comparison of Optional Inside Surface Flux Results

For software applying the 16 alternative 1-D conduction paths specified for this test case, total surface fluxes (q,x,tot) derived from measurements are provided in the file ET100series-MeasBasedSurfFlux-GMT+1.xlsx, see tab ‘ET110A’. Format of this file is provided in Table 5a.

For the purpose of this comparison, data is only provided for the best steady-state period; see the last 18 rows of ET100series-MeasBasedSurfFlux-GMT+1.xlsx, tab ‘ET110A’.

Informative Notes:

- These fluxes are provided for the purpose of comparing best-steady-state-period modeled individual conduction-path inside surface fluxes to measurement-based individual conduction-path heat fluxes derived from empirical measurements.

- At steady state, modeled total inside surface fluxes and measurement-based individual conduction-path heat fluxes should be approximately equal.

- Derivation of hourly q,x,tot at best steady-state is provided in ET100series-MeasBasedSurfFlux-GMT+1.xlsx, tab ‘ET110A-SurfFluxDeriv’. Determination of measured UA values applied for this derivation is described in Appendix C; see “SupplementaryFiles” folder within the accompanying electronic media.

- Table 5a.  Cell A Hourly Measurement-Based Heat-Flux File Format

| Column | Label | Description | Units |
| --- | --- | --- | --- |
| A | Date | Date and time in format “MM-DD-YYYY hh:mm” (preceding hour format, e.g., Hour 10:00 = 09:00-10:00) |  |
| B | q,c1,tot | Ceiling Path 1 | Wh/m2 |
| C | q,c2,tot | Ceiling Path 2 | Wh/m2 |
| D | q,f1,tot | Floor Path 1 | Wh/m2 |
| E | q,f2,tot | Floor Path 2 | Wh/m2 |
| F | q,f3,tot | Floor Path 3 | Wh/m2 |
| G | q,n,tot | North wall | Wh/m2 |
| H | q,d,tot | Door | Wh/m2 |
| I | q,e,tot | East wall | Wh/m2 |
| J | q,ewin1,tot | East window Path 1 | Wh/m2 |
| K | q,ewin2,tot | East window Path 2 | Wh/m2 |
| L | q,ewin3,tot | East window Path 3 | Wh/m2 |
| M | q,s,tot | South wall | Wh/m2 |
| N | q,swin1,tot | South window Path 1 | Wh/m2 |
| O | q,swin2,tot | South window Path 2 | Wh/m2 |
| P | q,swin3,tot | South window Path 3 | Wh/m2 |
| Q | q,w,tot | West wall | Wh/m2 |

#### Building Geometrical Description, Plans, Characteristics

##### Geometry

Cell A shall be defined initially.

Two options for modeling guard zones are specified depending on the capabilities of the tested programs:

- guard zones modeled as boundary conditions on the exterior side of each test cell bounding surface (Section 2.2.1.7.1.1)

- guard zones modeled as separate zones adjacent to the test cell bounding surfaces (Section 2.2.1.7.1.3).

Informative Note: Defining guard zones as boundary conditions is recommended because:

- Hourly guard zone measured air temperature data is provided

- It is simpler than modeling six guard zones (less potential for input errors)

- While the test cell construction is well defined, the guard zone constructions (except for relevant walls comprising their boundaries with the test cell) are approximate.

###### Summary geometry for models applying guard zones as boundary conditions

For programs that require modeling the guard zones as actual physical zones, see the instructions of Sections 2.2.1.7.1.2 and 2.2.1.7.1.3, and skip the remainder of this section.

As shown in Figure 1, the building is oriented 30° E of North, so that the test cell bounding surface that would nominally be called the "South” wall is oriented at 30° West of South, and the other walls are oriented and named accordingly with orientations offset 30° from their nominal cardinal directions.

Figure 1 also shows the plan view and a sectional view of Cell A and indicates the names of its six guard zones. These names are associated with hourly data identifiers within the accompanying file ET110A-Measurements-GMT+1.csv (see previous Section 2.2.1.3.1); e.g., “Tsouth” designates the south guard zone temperature data provided in column F of the file.

Other information for defining the guard zones as boundary conditions, related to surface heat transfer and additional supporting data, are provided in Sections 2.2.1.7.4 (Surface Heat Transfer) and 2.2.1.7.9 (Thermal Guards).

Informative Note: Figure 1 is a simplification based on the overall test cell floor plan from its original documentation (Girault and Guyon 1999; Neymark et al 2004).

N

Elevation Section View (looking 30° south of east through page)

Plan View

Figure 1: ETNA Cell A, Summary Diagrams with Artificial-Climate Thermal Guards

Note 1: Cell A internal dimension details are provided in Figure 2.

Note 2: Attic and cellar also fully cover ceiling and floor, respectively, of Cell A and west guard.

2.2.1.7.1.2  Test cell detailed geometry

The following sections specify the geometry of the test cell and its individual bounding surfaces and subsurfaces:

- Cell A primary inside surfaces (see Section 2.2.1.7.1.2.1); interior surface dimensions for the west wall, floor, and ceiling are taken directly from the figure in this section

- South wall and window (see Section 2.2.1.7.1.2.2)

- (Section 2.2.1.7.1.2.3 intentionally blank)

- East wall and window (see Section 2.2.1.7.1.2.4)

- North wall and door (see Section 2.2.1.7.1.2.5)

- Surface area summary (see Section 2.2.1.7.1.2.6).

Within these sections dimensions are provided in meters (m).

            - Cell A primary inside surfaces.

Figure 2 specifies the inside-surface (interior) dimensions of Cell A.   Interior surface dimensions for the west wall, floor, and ceiling are taken directly from this figure.

Floor

West Wall

Figure 2 Inside-Surface Dimensions of Cell A

Note: Ceiling is at 2.565 m height, parallel to floor, with same dimensions as floor

###### South wall and window

Figure 3 specifies the south wall geometry as viewed from the exterior, including the position of the window in the south wall, and the dimensions of the window glazing panels and framework.

Informative Note: In artificial climate cases, such as the ET110A1 base case, the windows may be modeled as walls, or subsections of walls, because there is no transmitted solar radiation.

Figure 3: Dimensioned south wall with window elevation, exterior view

2.2.1.7.1.2.3 Reserved

2.2.1.7.1.2.4  East wall and window

Figure 4 specifies the east wall geometry as viewed from the exterior, including the position of the window in the east wall and the dimensions of the window glazing panels and framework.

Informative Note: In artificial climate cases, such as the ET110A1 base case, the windows may be modeled as walls, or subsections of walls, because there is no transmitted solar radiation.

Figure 4: Dimensioned east wall with window elevation, exterior view

2.2.1.7.1.2.5  North wall and door.

Figure 5 specifies the north wall geometry as viewed from the exterior, including the position of the door in the north wall.

Figure 5: Dimensioned north wall and door elevation, exterior view

2.2.1.7.1.2.6  Surface area summary.

Table 6 summarizes the component surface areas for each Cell A bounding surface type, along with overall totals for a given wall. This table includes the sub-areas for the 16 alternative 1-D conduction paths shown in bold font that are defined with the construction details of Section 2.2.1.7.2, as summarized in Section 2.2.1.7.2.1.2.

Informative Note: This table is intended for checking geometry inputs by comparing tested-program intermediate geometry output with this table.

Table 6 Cell A Boundary-Surface Areas a,b

a. Sub-areas for the 16 alternative 1-D conduction paths defined in Section 2.2.1.7.2 are shown in bold font.

b. Author Note[tk]: Source file = “Surface Area Check (080423).xlsx” in “/SupplementaryFiles”, not included with accompanying files.

2.2.1.7.1.3  Alternative geometry for programs that require physically defining the guard zones

Users that apply guard zones as boundary conditions (per Section 2.2.1.7.1.1) in place of physically defining guard zone geometry and material constructions shall skip this section and continue with Section 2.2.1.7.2.

Figures 6 through 8 shall be applied for programs that require modeling the guard zones as actual physical zones. These figures show the plan view and section views of Cell A and its six guard zones, along with guard zone dimensions; see Figure 2 of Section 2.2.1.7.1.2.1 for test cell dimensions.

As shown in Figure 6, the building is oriented 30° E of North, so that the test cell bounding surface that would nominally be called the “South” wall is oriented at 30° West of South, and the other walls are oriented and named accordingly with orientations offset 30° from their nominal cardinal directions.

Informative Note: Figure 6 shows both test cells, Cell A and Cell B, in case full facility detail is needed for developing a model with physically defined guard zones.

Figures 6 through 8 also indicate the names of each guard zone. These names are associated with hourly data identifiers within the accompanying file ET110A-Measurements-GMT+1.csv (see previous Section 2.2.1.3.1); e.g., “Tsouth” designates the south guard zone temperature data provided in column F of the file.

Informative Notes:

- The details of the guard zones are incomplete (see Section 2.2.1.7.9) relative to the level of detail provided for the test-cell zones. During development of the test specification, project-team modelers developed exterior-surface boundary conditions for each test-cell surface based on the given guard zone temperatures (see Section 2.2.1.3) and exterior surface heat transfer coefficients (see Section 2.2.1.7.4). Programs that require modeling of the guard zones (that do not allow definition of test-cell exterior surface boundary conditions) should develop models of the guard zones based on the dimensions provided in Figures 6 through 8 and approximate material descriptions of Section 2.2.1.7.9.

- Guard zone dimensions include estimates based on drawings provided in Neymark et al. (2004), Figures 2 through 4, which are based on Girault and Guyon (1999), Figures 6 through 8.

See Note a.

See Note a.

Figure 6: Alternative summary geometry with guard zone dimensions: plan

Note a. For Cell A, this corner is either at north guard or west guard conditions or unconditioned depending on guard zone entry door positions, which were not recorded. Similarly for Cell B, the marked corner is either at north guard or east guard conditions or unconditioned depending on guard zone entry door positions, which were not recorded.

Figure 7 Alternative summary geometry with guard zone dimensions: Cell A elevation section looking 30° north of west through page

Notes for Figure 7:

The section/elevation for Cell B is the same as that shown here for Cell A, except the guard zone just north of the north guard is the “west” guard (see Figure 6 plan view).

The ground level of the cell is raised by 0.90 m above grade. The external walls of the cell are surrounded by thermal guards (either fully or partly depending on their configuration).

Figure 8: Alternative summary geometry with guard zone dimensions: elevation section looking 30° east of north through page

Notes:

- This section is cut along the apex of the attic roof.

###### 2.2.1.7.2  Test Cell Bounding Surface Material Constructions

The following sections specify material constructions of the test cell bounding surfaces and subsurfaces:

- Construction modeling options (Section 2.2.1.7.2.1)

- North wall (Section 2.2.1.7.2.2)

- East wall (Section 2.2.1.7.2.3)

- South wall (Section 2.2.1.7.2.4)

- West wall (Section 2.2.1.7.2.5)

- Ceiling (Section 2.2.1.7.2.6)

- Floor (Section 2.2.1.7.2.7)

- Door within north wall (Section 2.2.1.7.2.8)

- Window and insulation module within east and south walls (Section 2.2.1.7.2.9)

###### 2.2.1.7.2.1 Construction Modeling Options

In the following sections for each bounding surface, construction specifications are presented as required characteristics and alternative construction specifications.

2.2.1.7.2.1.1 Required characteristics include:

- Empirically determined UA values

- Construction details, as shown in the figures.

2.2.1.7.2.1.2 Alternative construction specifications consist of material properties tables that include:

- Catalog values

- Imputed thermal conductivities for selected material layers; imputed values are highlighted in yellow.

- 16 parallel 1-D conduction paths applied for determining the imputed thermal conductivities.

Informative Notes:

- Material property tables in the following sections are intended for simulations applying 1-dimensional thermal diffusion models, and are derived based on the interior surface area of a given bounding surface.

- Imputed properties are only valid for the given conduction paths.

- The alternative construction specifications are recommended for use based on Section 2.1.10.

- Informative Appendix C describes calculation of imputed values; see “SupplementaryFiles” folder within the accompanying electronic media.

2.2.1.7.2.2  North Wall

2.2.1.7.2.2.1 Required characteristics

The north wall, which is the bounding surface between the test cell and the North Guard zone, shall have the following characteristics:

- UA = 6.06 W/K. Informative Note: See Appendix C for supporting information.

- Construction as shown in Figure 9.

- Geometry as described in Figure 5 (see Section 2.2.1.7.1.2.5).

Construction of the door within the north wall is described separately in Section 2.2.1.7.2.8.

For modelers requiring further guidance to specify inputs of material properties, apply the alternative construction specification of Section 2.2.1.7.2.2.2 (following). Informative Note: Use of the Section 2.2.1.7.2.2.2 alternative is recommended (see Section 2.1.10).

2.2.1.7.2.2.2 Alternative construction specification

2.2.1.7.2.2.2.1 If the modeler does not require further guidance to develop inputs as specified in Section 2.2.1.7.2.2.1, skip the remaining instructions and proceed to Section 2.2.1.7.2.3.

2.2.1.7.2.2.2.2 The north wall is a single 1-D conduction path, corresponding to the method for which thermal conductivities of selected material layers were externally imputed. Informative Note: See Appendix C for details regarding external imputation of thermal conductivities.

Table 7 provides thermal properties and thicknesses with the material layer adjacent to the inside of the test cell at the top of the table, and then layers incrementally toward the guard zone for each row going down the table.

Figure 9: Sectional view of the North wall

Table 7: Characteristics of the North wall

(Net inside surface area = 7.1494 m²)

| Material | d Thickness [m] | k Conductivity [W/m.K] | Density [kg/m3] | Cp Specific heat [J/kg.K] |
| --- | --- | --- | --- | --- |
| Wallpaper | 0.001 | 0.14 | 700 | 1340 |
| Plasterboard | 0.013 | 0.35 | 850 | 800 |
| Air / Honeycomb Cardboard | 0.046 | 0.307a | 26.1 | 1340 |
| Plasterboard | 0.013 | 0.35 | 850 | 800 |
| Wallpaper | 0.001 | 0.14 | 700 | 1340 |
| Styrodur | 0.060 | 0.0563 b | 18 | 1200 |

a. Equivalent conductivity with regard to the air. See ASHRAE (2021a).

b. Imputed conductivity input highlighted in yellow based on Appendix C.

2.2.1.7.2.3  East Wall

2.2.1.7.2.3.1 Required characteristics

The east wall, which is the bounding surface between the test cell and the East Guard zone, shall have the following characteristics:

- UA values:

  - UA = 9.36 W/K; total east wall + window, measured without window insulation

  - UA = 6.86 W/K; total east wall + window with window insulation (see Section 2.2.1.7.2.9).

  - Informative Note: See Appendix C for supporting information.

- Construction as shown in Figure 10.

- Geometry as described in Figure 4 (see Section 2.2.1.7.1.2.4).

Construction of the window and its insulation module within the east wall is described separately in Section 2.2.1.7.2.9.

For modelers requiring further guidance to specify inputs of material properties, apply the alternative construction specification of Section 2.2.1.7.2.3.2 (following). Informative Note: Use of the Section 2.2.1.7.2.3.2 alternative is recommended (see Section 2.1.10).

2.2.1.7.2.3.2 Alternative construction specification

2.2.1.7.2.3.2.1 If the modeler does not require further guidance to develop inputs as specified in Section 2.2.1.7.3.2.1, skip the remaining instructions and proceed to Section 2.2.1.7.2.4.

2.2.1.7.2.3.2.2 The east wall is a single 1-D conduction path, corresponding to the method for which thermal conductivities of selected material layers were externally imputed. Informative Note: See Appendix C for details regarding external imputation of thermal conductivities.

Table 8 provides thermal properties and thicknesses with the material layer adjacent to the inside of the test cell at the top of the table, and then layers incrementally toward the guard zone for each row going down the table.

Figure 10: Sectional view of the East and South walls

Table 8: Characteristics of the East wall.

(Net inside surface area = 10.1378 m²)

| Material | d Thickness [m] | k Conductivity [W/m.K] | Density [kg/m3] | Cp Specific heat [J/kg.K] |
| --- | --- | --- | --- | --- |
| Wallpaper | 0.001 | 0.14 | 700 | 1340 |
| Plasterboard | 0.010 | 0.35 | 850 | 800 |
| Polystyrene | 0.080 | 0.0407 a | 15 | 1200 |
| Air gap | 0.010 | 0.070 b | 1.2 | 1000 |
| Hollow block | 0.200 | 1.052 | 1200 | 950 |
| Facing | 0.020 | 1.15 | 1950 | 850 |

a. Imputed conductivity input highlighted in yellow based on Appendix C; see “SupplementaryFiles” folder within the accompanying electronic media.

b. Equivalent conductivity with regard to the air. See ASHRAE (2021a)

2.2.1.7.2.4 South Wall

2.2.1.7.2.4.1 Required characteristics

The south wall, which is the bounding surface between the test cell and the South Guard zone, shall have the following characteristics:

- UA values:

  - UA = 8.07 W/K; total south wall + window, measured without window insulation

  - UA = 5.57 W/K; total south wall + window with window insulation (see Section 2.2.1.7.2.9).

  - Informative Note: See Appendix C for supporting information.

- Construction layers as shown in Figure 10 (see Section 2.2.1.7.2.3), similarly to the east wall, but with different UA-value and surface area (see bullets above and below, respectively).

- Geometry as described in Figure 3 (see Section 2.2.1.7.1.2.2).

Construction of the window and its insulation module within the south wall is described separately in Section 2.2.1.7.2.9.

For modelers requiring further guidance to specify inputs of material properties, apply the alternative construction specification of Section 2.2.1.7.2.4.2 (following). Informative Note: Use of the Section 2.2.1.7.2.4.2 alternative is recommended (see Section 2.1.10).

2.2.1.7.2.4.2 Alternative construction specification

2.2.1.7.2.4.2.1 If the modeler does not require further guidance to develop inputs as specified in Section 2.2.1.7.4.2.1, skip the remaining instructions and proceed to Section 2.2.1.7.2.5.

2.2.1.7.2.3.4.2 The south wall is a single 1-D conduction path, corresponding to the method for which thermal conductivities of selected material layers were externally imputed. Informative Note: See Appendix C for details regarding external imputation of thermal conductivities.

Table 9 provides thermal properties and thicknesses, with the material layer adjacent to the inside of the test cell at the top of the table, and then layers incrementally toward the guard zone for each row going down the table.  Informative Note: The material properties of Table 9 are the same as that for the East wall (see Table 8), except for different imputed conductivity of selected materials; see the yellow-highlighted values in Table 9.

Table 9: Characteristics of the South wall

(Net inside surface area = 7.1752 m²)

| Material | d Thickness [m] | k Conductivity [W/m.K] | Density [kg/m3] | Cp Specific heat [J/kg.K] |
| --- | --- | --- | --- | --- |
| Wallpaper | 0.001 | 0.14 | 700 | 1340 |
| Plasterboard | 0.010 | 0.35 | 850 | 800 |
| Polystyrene | 0.080 | 0.0383 a | 15 | 1200 |
| Air gap | 0.010 | 0.070 b | 1.2 | 1000 |
| Hollow block | 0.200 | 1.052 | 1200 | 950 |
| Facing | 0.020 | 1.15 | 1950 | 850 |

a. Imputed conductivity input highlighted in yellow based on Appendix C.

b. Equivalent conductivity with regard to the air. See ASHRAE (2021a).

2.2.1.7.2.5  West Wall

2.2.1.7.2.5.1 Required characteristics

The west wall, which is the bounding surface between the test cell and the West Guard zone, shall have the following characteristics:

- UA = 3.44 W/K. Informative Note: See Appendix C for supporting information.

- Construction as shown in Figure 11.

- Geometry as described in Figure 2 (see Section 2.2.1.7.2.1).

For modelers requiring further guidance to specify inputs of material properties, apply the alternative construction specification of Section 2.2.1.7.2.5.2 (following). Informative Note: Use of the Section 2.2.1.7.2.5.2 alternative is recommended (see Section 2.1.10).

2.2.1.7.2.5.2 Alternative construction specification

2.2.1.7.2.5.2.1 If the modeler does not require further guidance to develop inputs as specified in Section 2.2.1.7.5.2.1, skip the remaining instructions and proceed to Section 2.2.1.7.2.6.

2.2.1.7.2.5.2.2 The west wall is a single 1-D conduction path, corresponding to the method for which thermal conductivities of selected material layers were externally imputed. Informative Note: See Appendix C for details regarding external imputation of thermal conductivities.

Table 10 provides thermal properties and thicknesses with the material layer adjacent to the inside of the test cell at the top of the table, and then layers incrementally toward the guard zone for each row going down the table.

Figure 11: Sectional view of the West wall

Table 10: Characteristics of the West wall

(Net inside surface area = 11.9401 m²)

| Material | d Thickness [m] | k Conductivity [W/m.K] | Density [kg/m3] | Cp Specific heat [J/kg.K] |
| --- | --- | --- | --- | --- |
| Wallpaper | 0.001 | 0.14 | 700 | 1340 |
| Plasterboard | 0.010 | 0.35 | 850 | 800 |
| Polystyrene | 0.080 | 0.0597 a | 15 | 1200 |
| Air gap | 0.010 | 0.070 b | 1.2 | 1000 |
| Hollow block | 0.200 | 1.052 | 1200 | 950 |
| Air gap | 0.010 | 0.070 b | 1.2 | 1000 |
| Polystyrene | 0.080 | 0.0597 a | 15 | 1200 |
| Plasterboard | 0.010 | 0.35 | 850 | 800 |
| Wallpaper | 0.001 | 0.14 | 700 | 1340 |

a. Imputed conductivity input highlighted in yellow based on Appendix C.

b. Equivalent conductivity with regard to the air. See ASHRAE (2021a).

2.2.1.7.2.6  Ceiling

2.2.1.7.2.6.1 Required characteristics

The ceiling, which is suspended under the attic guard zone, shall have the following characteristics:

- UA = 2.67 W/K. Informative Note: See Appendix C for supporting information.

- Construction as shown in Figure 12a

- Geometry as described in Figure 2 (see Section 2.2.1.7.1.2.1).

For modelers requiring further guidance to specify inputs of material properties, apply the alternative construction specification of Section 2.2.1.7.2.6.2 (following). Informative Note: Use of the Section 2.2.1.7.2.6.2 alternative is recommended (see Section 2.1.10).

2.2.1.7.2.6.2 Alternative construction specification

2.2.1.7.2.6.2.1 If the modeler does not require further guidance to develop inputs as specified in Section 2.2.1.7.2.6.1, skip the remaining instructions and proceed to Section 2.2.1.7.2.7.

2.2.1.7.2.6.2.2 The ceiling shall be divided into two parallel 1-D conduction path segments, corresponding to the method for which thermal conductivity of selected material layers were externally imputed. Informative Note: See Appendix C for details regarding external imputation of thermal conductivities.

Figure 12b illustrates the two parallel 1-d conduction heat flow paths (Path 1 and Path2) to be applied in the simulations.

Tables 11a and 11b provide the thermal properties and thicknesses for each material layer of each parallel path (Path 1 and Path 2, respectively for each table), with the layer adjacent to the inside of the test cell at the top of the table, and then layers incrementally toward the guard zone for each row going down the table. Net inside surface area for each heat flow path is provided, respectively, in each table caption.

Figure12a: Sectional view of the ceiling (partial)

Notes:

- The cross-section area of the ceiling planks (joists) is the equivalent of 9 joists, traversing east-west (see Table 6, Section 2.2.1.7.1.2.6).

- Informative Note: This is a simplification of the original figure; see Appendix C for details (see “SupplementaryFiles” folder within the accompanying electronic media).

Figure 12b: Section/elevation view (same view as Figure 12a) of the ceiling heat-flow paths

Table 11a: Characteristics of the ceiling – Path 1

(Net inside surface area = 14.4025 m²)

| Material | d Thickness [m] | k Conductivity [W/mK] | ρ Density [kg/m3] | Cp Specific heat [J/kgK] |
| --- | --- | --- | --- | --- |
| Wallpaper | 0.001 | 0.14 | 700 | 1340 |
| Plasterboard | 0.013 | 0.35 | 850 | 800 |
| Glass wool 1 | 0.200 | 0.0364 a | 11 | 800 |
| Air gap | 0.100 | 0.618 b | 1.2 | 1000 |
| Particle board | 0.021 | 0.17 | 700 | 1200 |

a. Imputed conductivity input highlighted in yellow based on Appendix C.

b. Equivalent conductivity with regard to the air. See ASHRAE (2021a).

Table 11b: Characteristics of the ceiling – Path 2

(Net inside surface area = 1.8900 m²)

| Material | d Thickness [m] | k Conductivity [W/mK] | ρ Density [kg/m3] | Cp Specific heat [J/kgK] |
| --- | --- | --- | --- | --- |
| Wallpaper | 0.001 | 0.14 | 700 | 1340 |
| Plasterboard | 0.013 | 0.35 | 850 | 800 |
| Glass wool 2 | 0.150 | 0.0364 a | 11 | 800 |
| Planks | 0.150 | 0.15 | 500 | 1200 |
| Particle board | 0.021 | 0.17 | 700 | 1200 |

a. Imputed conductivity input highlighted in yellow based on Appendix C.

##### 2.2.1.7.2.7  Floor

2.2.1.7.2.7.1 Required characteristics

The floor, which is suspended over the Cellar guard zone, shall have the following characteristics:

- UA = 6.32 W/K. Informative Note: See Appendix C for supporting information.

- Construction as shown in Figure 13a.

- Geometry as described in Figure 2 (see Section 2.2.1.7.1.2.1).

For modelers requiring further guidance to specify inputs of material properties, apply the alternative construction specification of Section 2.2.1.7.2.7.2 (following). Informative Note: Use of the Section 2.2.1.7.2.7.2 alternative is recommended (see Section 2.1.10).

2.2.1.7.2.7.2 Alternative construction specification

2.2.1.7.2.7.2.1 If the modeler does not require further guidance to develop inputs as specified in Section 2.2.1.7.2.7.1, skip the remaining instructions and proceed to Section 2.2.1.7.2.8.

2.2.1.7.2.7.2.2 The floor is divided into three parallel 1-D conduction path segments, corresponding to the method for which thermal conductivities of selected material layers were externally imputed. Informative Note: See Appendix C for details regarding external imputation of thermal conductivities.

Figure 13b illustrates the three parallel 1-d conduction heat flow paths (Path 1, Path2, and Path 3) to be applied in the simulations.

Tables 12a, 12b, and 12c provide thermal properties and thicknesses for each material layer of each parallel path (Path 1, Path 2, and Path 3, respectively for each table), with the layer adjacent to the inside of the test cell at the top of the table, and then layers incrementally toward the guard zone for each row going down the table. Net inside surface area for each heat flow path is provided, respectively, in each table caption.

Figure 13a: Section/elevation view of the floor

Notes:

- The cross-section area of the floor concrete beam components is equivalent to 7 concrete beams traversing east-west (see Table 6, Section 2.2.1.7.1.2.6).

- Informative Note: The “Concrete+Tubes+Polysty Ribs” in the upper portion of this figure is a simplification of the original test spec floor figures (Neymark et al. 2004, Girault and Guyon 1999); also see Appendix C. The floor has the capability to be a hydronic heating/cooling radiative floor (water and heat pump). Radiant floor heating/cooling was inactive during these tests, with no water present in the hydronic tubes. For the construction of the material layer containing the hydronic tubes, Tables 12a, 12b, and 12c provide a simplified aggregation; see note “a”[tk] of the tables.

Figure 13b: Section/elevation view (same view as Figure 13a) of the floor parallel heat-flow paths

Table 12a: Characteristics of the floor – Path 1

(Net inside surface area = 13.3525 m²)

| Material | d Thickness [m] | k Conductivity [W/mK] | Density [kg/m3] | Cp Specific heat [J/kgK] |
| --- | --- | --- | --- | --- |
| Ceramic Tile | 0.006 | 1.75 | 2177 | 920 |
| Glue Cement | 0.003 | 1.50 | 1900 | 840 |
| Concrete | 0.008 | 1.75 | 2177 | 920 |
| Concrete + Tubes + Polysty Ribs a | 0.016 | 1.47 | 1813 | 954 |
| Polystyrene 1 | 0.035 | 0.0719 b | 16 | 1200 |
| Plastic Lining | 0.002 | 0.124 | 265 | 1170 |
| Concrete Slab | 0.065 | 1.75 | 2200 | 950 |
| Insulated Block 1 | 0.070 | 0.0719 b | 18 | 1200 |
| Insulated Block 2 | 0.050 | 0.0719 b | 18 | 1200 |
| Polystyrene 2 | 0.030 | 0.0719 b | 18 | 1200 |
| Plasterboard | 0.013 | 0.35 | 850 | 800 |

a. Based on Figure 13a, for simplification, layer properties here assume a by-volume-averaged blended layer of concrete, polystyrene, tubes, and air within empty tubes. Documentation of how this layer was calculated is included in Appendix C.

b. Imputed conductivity input highlighted in yellow based on Appendix C.

Table 12b: Characteristics of the floor – Path 2

(Net inside surface area = 1.4700 m²)

| Material | d Thickness [m] | k Conductivity [W/mK] | Density [kg/m3] | Cp Specific heat [J/kgK] |
| --- | --- | --- | --- | --- |
| Ceramic Tile | 0.006 | 1.75 | 2177 | 920 |
| Glue Cement | 0.003 | 1.50 | 1900 | 840 |
| Concrete | 0.008 | 1.75 | 2177 | 920 |
| Concrete + Tubes + Polysty Ribs a | 0.016 | 1.47 | 1813 | 954 |
| Polystyrene 1 | 0.035 | 0.0719 b | 16 | 1200 |
| Plastic Lining | 0.002 | 0.124 | 265 | 1170 |
| Concrete Slab | 0.065 | 1.75 | 2200 | 950 |
| Insulated Block 1 | 0.070 | 0.0719 b | 18 | 1200 |
| Concrete Beam 2 | 0.050 | 1.75 | 2200 | 950 |
| Polystyrene 2 | 0.030 | 0.0719 b | 18 | 1200 |
| Plasterboard | 0.013 | 0.35 | 850 | 800 |

a. Based on Figure 13a, for simplification, layer properties here assume a by-volume-averaged blended layer of concrete, polystyrene, tubes, and air within empty tubes. Documentation of how this layer was calculated is included in Appendix C.

b. Imputed conductivity input highlighted in yellow based on Appendix C.

Table 12c: Characteristics of the floor – Path 3

(Net inside surface area = 1.4700 m²)

| Material | d Thickness [m] | k Conductivity [W/mK] | Density [kg/m3] | Cp Specific heat [J/kgK] |
| --- | --- | --- | --- | --- |
| Ceramic Tile | 0.006 | 1.75 | 2177 | 920 |
| Glue Cement | 0.003 | 1.50 | 1900 | 840 |
| Concrete | 0.008 | 1.75 | 2177 | 920 |
| Concrete + Tubes + Polysty Ribs a | 0.016 | 1.47 | 1813 | 954 |
| Polystyrene 1 | 0.035 | 0.0719 b | 16 | 1200 |
| Plastic Lining | 0.002 | 0.124 | 265 | 1170 |
| Concrete Slab | 0.065 | 1.75 | 2200 | 950 |
| Concrete Beam 1 | 0.070 | 1.75 | 2200 | 950 |
| Concrete Beam 2 | 0.050 | 1.75 | 2200 | 950 |
| Polystyrene 2 | 0.030 | 0.0719 b | 18 | 1200 |
| Plasterboard | 0.013 | 0.35 | 850 | 800 |

a. Based on Figure 13a, for simplification, layer properties here assume a by-volume-averaged blended layer of concrete, polystyrene, tubes, and air within empty tubes. Documentation of how this layer was calculated is included in Appendix C.

b. Imputed conductivity input highlighted in yellow based on Appendix C.

2.2.1.7.2.8  Door within north wall

2.2.1.7.2.8.1 Required characteristics

The door shall have the following characteristics:

- Construction as shown in Figure 14, which illustrates the insulation module that fits over the door from the outside.

- Geometry as described in Figure 5 (see Section 2.2.1.7.1.2.5).

For modelers requiring further guidance to specify inputs of material properties, apply the alternative construction specification of Section 2.2.1.7.2.8.2 (following). Informative Note: Use of the Section 2.2.1.7.2.8.2 alternative is recommended (see Section 2.1.10).

2.2.1.7.2.8.2 Alternative construction specification

2.2.1.7.2.8.2.1 If the modeler does not require further guidance to develop inputs as specified in Section 2.2.1.7.2.8.1, skip the remaining instructions and proceed to Section 2.2.1.7.2.9.

2.2.1.7.2.8.2.2 The door is a single 1-D conduction path, corresponding to the method for which thermal conductivities of selected material layers were externally imputed. Informative Note: See Appendix C for details regarding external imputation of thermal conductivities.

Table 13 provides thermal properties and thicknesses for each material layer, with the layer adjacent to the inside of the test cell at the top of the table, and then layers incrementally toward the guard zone for each row going down the table.

Informative Notes:

- This is a simplified version of the door that allows it to be modeled as a single 1-D conduction path. See Appendix C for supporting details.

- Empirical determination of disaggregated door UA is not available. See Section 2.2.1.7.2.2 for empirically determined UA of the overall north wall including the door.

Door insulation module

- There is one 0.060 m-thick layer of styrodur constructed such that there is a 0.038 m air gap between the inner surface of the insulation module and a simplified blended material layer; see horizontal section below.

- Door styrodur and wall styrodur have the same thermal properties.

- Informative Note: This simplification of the actual construction is intended to reduce the greater chance for input errors with the more complicated actual construction. See Appendix C for greater detail.

Horizontal Section, Door A and B

Figure 14.  Door Insulation

Table 13: Characteristics of the door

(Net inside surface area = 1.8281 m²)

| Material | d Thickness [m] | k Conductivity [W/m.K] | Density [kg/m3] | Cp Specific heat [J/kg.K] |
| --- | --- | --- | --- | --- |
| Blended Wood/Air/Cardboard + Plywood + Plexiglassa | 0.036 | 0.1643 b | 307 | 1317 |
| Blended Air Gapa | 0.038 | 0.254 c | 1.2 | 1000 |
| Styrodur (see Figure 14) | 0.060 | 0.0563 b | 18 | 1200 |

a. See Appendix C for supporting information.

b. Imputed conductivity inputs highlighted in yellow based on Appendix C.

c. Equivalent conductivity with regard to air. See ASHRAE (2021a).

2.2.1.7.2.9  Window and insulation module within east and south walls

2.2.1.7.2.9.1 Required characteristics

Insulated windows are applied to both the south and east walls for the geometry shown in Figures 3 and 4 (see Sections 2.2.1.7.1.2.2 and 2.2.1.7.1.2.4), and shall have the following characteristics:

- UA = 2.50 W/K reduction to east and south wall uninsulated window UA values (see Sections 2.2.1.7.2.3 and 2.2.1.7.2.4, respectively) for installed window insulation module. Informative Note: See Appendix C for supporting information.

- Construction as shown in Figure 15a.

- A window insulation module fills the rough opening in each wall (see Figures 3 and 4); each insulation module is applied to the external side of the window within the setback cavity that sets the window inward from the wall exterior surface (see Figure 15a).

For modelers requiring further guidance to specify inputs of material properties, apply the alternative construction specification of Section 2.2.1.7.2.9.2 (following). Informative Note: Use of the Section 2.2.1.7.2.9.2 alternative is recommended (see Section 2.1.10).

2.2.1.7.2.9.2 Alternative construction specification

2.2.1.7.2.9.2.1 If the modeler does not require further guidance to develop inputs as specified in Section 2.2.1.7.2.9.1, skip the remaining instructions and proceed to Section 2.2.1.7.3.

2.2.1.7.2.9.2.2 The insulated window is divided into three parallel 1-D conduction path segments, corresponding to the method for which thermal conductivities of the selected material layers were externally imputed. Informative Note: See Appendix C for details regarding external imputation of thermal conductivities.

Figure 15b illustrates the three parallel 1-d conduction heat flow paths (Path 1, Path 2, and Path 3) to be applied in the simulations.

Tables 15a, 15b and 15c provide thermal properties and thicknesses for each material layer of each parallel path (Path 1, Path 2, and Path 3, respectively, for each table), with the layer adjacent to the inside of the test cell at the top of the table, and then layers incrementally toward the guard zone for each row going down the table. Net inside surface area for each heat flow path is provided, respectively, in each table caption.

Figure 15a: Window Vertical Section (window and frame assembly), through the window and external setback cavity looking downward (or upward) – NOT TO SCALE

- Notes: Informative Note: This figure is a simplification of the actual construction to reduce the greater chance for input errors with the more complicated actual construction. See Appendix C for greater detail.

Figure 15b: Window vertical section view (window and frame assembly) of the insulated window parallel heat-flow paths, looking downward (or upward) – NOT TO SCALE

Table 15a: Characteristics of insulated windows – Path 1

(Net inside surface area = 0.9905 m²)

| Material | d Thickness [m] | k Conductivity [W/m.K] | Density [kg/m3] | Cp Specific heat [J/kg.K] |
| --- | --- | --- | --- | --- |
| Blended Glass/Air Gap /Glass a | 0.020 | 0.124 | 1081 | 900 |
| Air Gap b | 0.009 | 0.1234 c | 1.2 | 1000 |
| Glasswool 1 | 0.200 | 0.0657 c | 11 | 800 |
| Polystyrene 1 | 0.070 | 0.0657 c | 16 | 1200 |

a. See Appendix C, Section C.5 for supporting information.

b. This air gap applies only to Path 1, i.e., the area over the glass pane as shown in Figures 15a and 15b.

c. Imputed conductivity input highlighted in yellow based on Appendix C.

Table 15b: Characteristics of insulated windows – Path 2

(Net inside surface area = 0.1385 m²)

| Material | d Thickness [m] | k Conductivity [W/m.K] | Density [kg/m3] | Cp Specific heat [J/kg.K] |
| --- | --- | --- | --- | --- |
| PVC | 0.062 | 0.16 | 1380 | 1000 |
| Glasswool 2 | 0.188 a | 0.0657 b | 11 | 800 |
| Polystyrene 1 | 0.070 | 0.0657 b | 16 | 1200 |

a. The glasswool against the window frame is compressed from a total thickness of 0.2 m to 0.188 m.

b. Imputed conductivity input highlighted in yellow based on Appendix C.

Table 15c: Characteristics of insulated windows – Path 3

(Net inside surface area = 0.6734 m²)

| Material | d Thickness [m] | k Conductivity [W/m.K] | Density [kg/m3] | Cp Specific heat [J/kg.K] |
| --- | --- | --- | --- | --- |
| Blended PVC + facing + plasterboard a | 0.062 | 3.3570 b,c | 1442 | 975 |
| Glasswool 3 d | 0.188 e | 2.6227 b,c | 316 | 808 |
| Polystyrene 2 d | 0.070 | 2.6227 b,c | 320 | 1145 |

a. As a modeling simplification, the Path-3 window frame material includes the external setback cavity facing (known thermal bridge) and the plasterboard covering the facing on the test cell interior surface; see Appendix C for supporting information.

b. Informative Note: For conduction heat transfer Path 3, all layers have greater imputed conductivities to account for 3-D conduction likely to occur because this path is a thermal bridge relative to the insulated window and opaque wall (see Tables 8, 9, 15a, and 15b).

c. Imputed conductivity input highlighted in yellow based on Appendix C.

d. As a modeling simplification, the Glasswool 3 and Polystyrene 2 materials include the external setback cavity facing (known thermal bridge); see Appendix C for supporting information.

e. The glasswool against the window frame is compressed from a total thickness of 0.2 m to 0.188 m.

##### 2.2.1.7.3  Surface Radiative Properties

Table 16 indicates the solar absorptivity and infrared emissivity values corresponding to the surfaces of Cell A.

Table 16 Surface Radiative Properties of Cell A a

| Opaque Surface | Interior Radiative Properties |  | Exterior Radiative Properties |  |
| --- | --- | --- | --- | --- |
|  | Solar Absorptivity | Infrared Emissivity/ Absorptivity | Solar Absorptivity | Infrared Emissivity/ Absorptivity |
| North wall | 0.343 | 0.870 | 0.3 | 0.9 |
| East wall | 0.343 | 0.870 | 0.419 | 0.919 |
| South wall | 0.343 | 0.870 | 0.419 | 0.919 |
| West wall | 0.343 | 0.870 | 0.343 | 0.870 |
| Ceiling | 0.343 | 0.870 | 0.3 | 0.9 |
| Floor | 0.249 | 0.846 | 0.3 | 0.9 |
| Door (North) | 0.439 | 0.872 | 0.439 | 0.872 |
| Insulated Window Glazing | 0.5b | 0.9 | 0.419 | 0.919 |
| Insulated Window Frame | 0.343 | 0.870 | 0.419 | 0.919 |

a. Properties are from Neymark et al. (2004), except where otherwise noted.

b. Rough estimate for unmeasured glass wool behind glazing.

2.2.1.7.4  Surface heat transfer

The constant interior and exterior combined convective and radiative surface coefficients (h,comb,int and h,comb,ext, respectively) of Table 17 shall be applied. Time-step varying calculation of surface heat transfer coefficients is prohibited. Use of constant values other than those of Table 17 is prohibited.

Table 17 Interior and Exterior Combined Surface Heat Transfer Coefficients of Cell A

|  | Interior Surface h,comb,int (W/(m2K)) | Exterior Surface h,comb,ext (W/(m2K)) |
| --- | --- | --- |
| North wall | 10.5 | 18 |
| East wall | 7.0 | 18 |
| South wall | 7.0 | 18 |
| West wall | 5.3 | 18 |
| Ceiling | 3.6 | 18 |
| Floor | 5.3 | 18 |
| Door (North) | 10.5 | 18 |
| Insulated Windows, East & South |  |  |
| Path 1 (through glass) | 7.0 | 18 |
| Path 2 (through inner frame) | 7.0 | 18 |
| Path 3 (through blended outer frame) | 12.0 | 18 |

Informative Notes:

- Values of Table 17 are based on measured data; see Appendix C for details.

- The values of Table 17 are applied to develop imputed thermal conductivities of various wall constructions of Section 2.2.1.7.2; see Appendix C for details.

- Informative Note: The greater coefficient of insulated window Path 3 shown in Table 17 is the same as that determined for the uninsulated window (see Section 2.2.5.9). This is for consistency with Path 3 having greater insulation conductivities to account for thermal bridging and 3-D conduction (see Table 15c, informative note b).

- For programs that allow direct input of constant convective surface coefficients but not direct input of constant combined (radiative and convective) surface coefficients, input may be entered as follows: enter the appropriate values for interior and/or exterior surfaces as convective coefficients, and set respective surface emittances to 0 (or as low as the program being tested allows).

- Constant surface coefficients presented here apply only to this test suite as they are specified for each test case and were determined only for the given test-case configurations; they should not be assumed to apply beyond this test suite.

2.2.1.7.5 Thermal Bridges

Informative Notes:

- Listed material thermal conductivity imputations based on measured surface UA values (specified in Section 2.2.1.7.2) are intended to incorporate as-constructed variations of actual thermal properties relative to nominal thermal properties, including variations caused by unspecified thermal bridges.

- Neymark et al. (2004), Appendix D includes details of junctions between surfaces.

2.2.1.7.6 Infiltration

Infiltration = 0 ACH.

Informative Note: Listed material thermal conductivity imputations based on measured surface UA values (specified in Section 2.2.1.7.2) are intended to incorporate as-constructed variations of overall thermal properties relative to nominal thermal properties, including variations caused by unintended infiltration air leaks.

2.2.1.7.7 Interior solar distribution

A consistent interior solar distribution modeling method shall be applied for all test cases.

Informative Note: In the artificial climate configuration, there is no incident solar radiation on any of the exterior surfaces of the actual test cell; therefore, there is no absorbed solar radiation on any of these surfaces and no transmitted solar radiation in the test cell.

2.2.1.7.8 Internal gains

For Case ET110A, hourly-integrated measured fan energy is included with the test data (see Section 2.2.1.3.1).

- Apply fan heat as a sensible internal gain that is 100% convective.

Informative Notes:

- For the ET110A data acquisition period, hourly fan energy ranges from 0 to 225 Wh/h.

- There are no other internal gains in the test cell (no lighting, no occupants, etc.).

2.2.1.7.9 Thermal Guards

While guard zone temperature data is fully available, guard zone construction details are approximate. Two methods of modeling guard zones are indicated depending on what the program being tested allows:

- For programs that allow guard zones to be modeled as bounding surface exterior boundary conditions, see Section 2.2.1.7.9.1

- For programs that require detailed modeling of guard-zone geometry (i.e., that do not have an option to model zones adjacent to the test cell as external boundary conditions), see Section 2.2.1.7.9.2

Informative Note: Modeling guard zones as exterior surface boundary conditions, as in Section 2.2.1.7.9.1, is recommended because such a model reduces complexity and therefore reduces the potential for input errors.

2.2.1.7.9.1 Modeling guard zones as exterior surface boundary conditions

- Apply separate guard-zone air temperatures to each test cell bounding surface as specified in Section 2.2.1.3

- Apply exterior combined surface heat transfer coefficients to test cell bounding surfaces as specified in Section 2.2.1.7.4.

- Skip the remaining instructions and proceed to Section 2.2.1.8

2.2.1.7.9.2 Detailed modeling of guard zone geometry and construction

2.2.1.7.9.2.1 Geometry.

Apply overall test cell geometry of Figures 6 through 8; see Section 2.2.1.7.1.3.

2.2.1.7.9.2.2 Constructions.

Construction details of the guard zones are not provided, other than for each guard zone’s surface in common with the test cell (primary surface) as described in Sections 2.2.1.7.2 (Cell A) and 2.2.3.6 (Cell B). Users shall develop an approximate model of each guard zone’s other surfaces based on the following qualitative descriptions.

2.2.1.7.9.2.2.1 North, East (Cell A), West (Cell B), Cellar, and Attics Guard Zones

The load bearing structure of these guard zones is a wooden structure (pine wood). Internal surfaces of the wall are covered with polystyrene and with plywood. The material used for external surfaces exposed to ambient weather conditions of the Cell A East, Cell B West, and Attic guards is metallic cladding.

Test cell windows (east window Cell A, west window Cell B) are shielded from direct infrared radiation exchange with the guard zone-to-ambient-bounded walls by large black plywood/insulation panels hung between walls and windows in the Cell A East and Cell B West guard zones, so that the guard zone air temperature is also appropriate for calculating infrared radiation exchange between the guard zone and the test cell windows.

Informative Notes:

1. North guard zones of Cell A and Cell B and generally other guards’ constructions are further informed by Neymark et al. (2004)

2. In Neymark et al. (2004) Figures 2 and 3, the following labeling is applied regarding the guard zones: “bisA” is Cell A North; “bisB” is Cell B North; “sas 1” is Cell A East; “sas 3” is Cell B West.

              - West (Cell A) and East (Cell B) guard zones

Informative Note: These guard zone constructions are further informed by Neymark et al. (2004), Figures 2 and 3, where in Figure 2 the following labeling is applied regarding the guard zones: “Calcul” is Cell A West; “Escalier” is Cell B East.

2.2.1.7.9.2.2.3 South Guard Zone

Artificial climate is achieved by use of a single large mobile thermal guard zone affixed to the south side (bounding the south walls) of both test cells. This mobile thermal guard is made up of four blocks, assembled together. The load bearing structure is a steel structure. Interior surfaces of the guard zone exterior walls are covered with polyurethane (thickness: 0.20 m).

In the south thermal guard zone, infrared radiation exchange from the guard-zone surfaces to the window was not directly shielded by black plywood/insulation panels.

Informative Note: In Neymark et al. (2004), Figure 2, “sas 2” is the mobile south guard.

2.2.1.7.9.2.3 Guard zone interior surface heat transfer

2.2.1.7.9.2.3.1 Surfaces comprising test cell boundary walls.

Apply exterior combined surface heat transfer coefficients to the exterior side of the test cell bounding surfaces as specified in Sections 2.2.1.7.4 (Cell A) and 2.2.3.8 (Cell B).

2.2.1.7.9.2.3.2 All other guard-zone interior surfaces.

Apply the exterior combined surface heat transfer coefficients specified in Sections 2.2.1.7.4 (Cell A) and 2.2.3.8 (Cell B) to the interior side of all guard zone bounding surfaces.

2.2.1.7.9.2.4 Exterior surface heat transfer: South, East (Cell A), West (Cell B), and Attic

For guard zones with exterior surfaces exposed to ambient conditions (having dynamic variation), the modeler shall select the following as allowed by their program:

- A time-step varying exterior surface convection heat transfer algorithm, or constant surface convection coefficient(s) applied to each exterior surface face

- A time-step varying exterior surface infrared radiation exchange algorithm.

2.2.1.7.9.2.4.1 Exterior Surface Texture.

For programs that allow variation of exterior surface heat transfer with surface texture, exterior surface texture shall be selected within the tested program consistent with the surface material indicated in Section 2.2.1.7.9.2.2.

2.2.1.7.9.2.5 Guard Zones Temperature Control and Data.

Apply separate guard-zone air temperatures to each guard zone as specified in Section 2.2.1.3.

Informative Note: A cooling/heating system controls the individual guard-zone temperatures separately for each test cell, except for the cellar and the south guard zones as follows:

- For the cellar, a single control set point regulates the cellar guard zone temperatures for both Cell A (TcellarA) and Cell B (TcellarB).  This resulted in an offset of about 0.1°C to 0.2°C between TcellarA and TcellarB.

- For the south guard zone, an individual cooling/heating system is installed in this guard zone and a single control point regulates the south guard zone temperatures for both Cell A (TsouthA) and Cell B (Tsouth2B). This resulted in an offset of about 0.2°C to 0.3°C between TsouthA and TsouthB.

Informative Note: Approximate set points are given in Neymark et al. (2004), Appendix B. Although the test cell temperatures are generally controlled within a range of 0.1°C, there is occasional drift outside that range. The guard zones exhibit somewhat greater temperature drift.

2.2.1.8 Mechanical System

Informative Notes:

- A mechanical system is specified to provide the sensible heating needed to maintain the modeled heating setpoint temperatures.

- For the purpose of the 1-D conduction test of ET110A, the mechanical system is idealized to match the assumptions applied during external imputation of selected thermal conductivities (see Section 2.2.1.7.2.1.2).

- The intent of the mechanical system is to:

  - Produce only pure heating load output

  - Emulate the well-mixed zone air assumption common to BPS software, while minimizing (providing realistic) interior convective surface heat transfer (predominantly buoyancy driven, which corresponds with low air velocities).

- Details of the mechanical system designed to emulate these idealizations are provided in Neymark et al. (2004), Sections 2.2.1.7.1.3 and 2.2.1.7.2.

2.2.1.8.1 Equipment Characteristics (Heater with Diffusers, HWD)

2.2.1.8.1.1  Heater Power Capacity and Efficiency

a) Capacity:

i) For programs with idealized mechanical systems that implicitly assume unlimited or nearly unlimited capacity, such capacity shall be allowed, and proceed to Item b.

ii) For programs that do not provide an idealized mechanical system that implicitly assumes unlimited or nearly unlimited capacity,  use the following for developing the heating capacity input to the software being tested:

Heating Capacity ≥ 1215 Wh/h

Informative Note: For the Period 1, Case ET110A data acquisition period, i.e., from 00-01-26-12:00 through 00-02-11-09:00 (GMT+1), maximum measured hourly-integrated heating energy in Cell A is 1214.40 Wh/h, and the measured heating power at steady state is less than the maximum measured heating power. As the method of the test case is for programs to maintain hourly test cell air temperature (Tcell), any heating capacity entered into the software that is sufficient to maintain Tcell throughout the test case data acquisition period – without creating other issues (e.g., model instability) that may arise from excessive oversizing – is satisfactory.

b) Efficiency:

- 100% efficient heater

- Equipment efficiency shall always be 100% independent of part loading, test-cell indoor dry-bulb temperature and humidity ratio, guard-zone dry-bulb temperature and humidity ratio, and/or other conditions

- No duct losses.

2.2.1.8.1.2 Estimated Radiative Fraction

Radiative fraction (F,rad) = 0

where, F,rad = (radiated energy)/(convected energy + radiated energy).

Informative Note: This represents an idealized 100% convective air system.

2.2.1.8.1.3  Fan Energy

Fan energy shall be modeled as an internal gain (see Section 2.2.1.7.8) and shall not be modeled explicitly as part of the mechanical system. If the program being tested requires an air-distribution fan, it shall be specified to consume no energy.

2.2.1.8.2 Thermostat

2.2.1.8.2.1 Thermostat Set Point.

a) Apply setpoint values for test-cell air temperatures and guard-zone air temperatures included in the data file specified in Section 2.2.1.3. Informative Note: For Cases ET110A, ET110B, ET100A, and ET100B, test cell air temperature set point = 35°C. Although the test cell temperatures are generally controlled within a range of 0.1°C, there is occasional drift outside that range.

b) If the simulation program being tested allows, input hourly test cell air (setpoint) temperatures using either a detailed setpoint schedule input or an external input file, developed from the hourly data.

2.2.1.8.2.2 Thermostat Control Features.

a) The thermostat shall sense only the test-cell air temperature. Informative Note: This is a bulk average air temperature shielded from infrared and solar radiation as described in Neymark et al. (2004), Figure 18 (Section 2.2.1.7.2).

b) The thermostat shall be nonproportional. Informative Note: A nonproportional thermostat operates such that when the conditioned zone air temperature drops below the thermostat heating set point, the heat addition rate is adjusted to maintain the zone air temperature exactly at the heating set point. A proportional thermostat throttles the heat addition rate (or extraction rate if there is cooling) in proportion to the difference between the zone set-point temperature and the actual zone temperature. A proportional thermostat model can be made to approximate a nonproportional thermostat model by setting a very small throttling range (the minimum allowed by the program being tested).

### Case ET110A2: Artificial Climate, Steady-State Overall Building Loss Coefficient with Insulated Windows, Cell A, Applying Specified Catalog Material Properties (No Imputed Properties)

#### Informative Note: Objective and Method of the Test Case

Case ET110A2 is specified as an extension case based on the artificial climate base case (Case ET110A1).

The catalog-only data case – where imputed insulation conductivities of the base case are replaced with nominal catalog values – is provided to:

- Indicate the importance of developing imputed conductivities assuming one-dimensional (1-D) conduction (what most models do) based on measured data versus applying only material properties from catalog data in otherwise the same model

- Allow modelers to run sensitivity tests to examine causes of the load differences between applying imputed conductivities and only catalog values (i.e., filling the gap in differences). Such sensitivities may include evaluating the effects of two-dimensional (2-D) or three-dimensional (3-D) conduction, construction imperfections, thermal bridges, surface heat transfer, etc.

For an idealized heating system (that effectively outputs building load), apply results comparisons as listed with Objectives and Methods for Case ET110A1; see Section 2.2.1.1 Informative Notes, Item 3.

#### Extension Case Basis

Case ET110A2 shall be modeled exactly the same as Case ET110A1 except for changes detailed in the following sections.

#### Output Requirements.

Provide output applying tab ET110A2 of the template ET100series-output-GMT+1….xlsx,  which is included with the accompanying electronic media. Output requirements and format of Section 2.2.1.6 (Case ET110A1) shall apply.

#### Test Cell Bounding Surface Material Constructions.

Changes shall be made to selected material thermal conductivities specified in Section 2.2.1.7.2; catalog values replacing imputed values from Case ET110A1 are indicated via footnotes and bold yellow-highlighted text in the following tables:

- Characteristics of the North wall: Table 18 replaces Table 7

- Characteristics of the East wall: Table 19 replaces Table 8

- Characteristics of the South wall: Table 20 replaces Table 9

- Characteristics of the West wall: Table 21 replaces Table 10

- Characteristics of the ceiling – Path 1: Table 22a replaces Table 11a

- Characteristics of the ceiling – Path 2: Table 22b replaces Table 11b

- Characteristics of the floor – Path 1: Table 23a replaces Table 12a

- Characteristics of the floor – Path 2: Table 23b replaces Table 12b

- Characteristics of the floor – Path 3: Table 23c replaces Table 12c

- Characteristics of the door: Table 24 replaces Table 13

- Characteristics of insulated windows – Path 1: Table 25a replaces Table 15a

- Characteristics of insulated windows – Path 2: Table 25b replaces Table 15b

- Characteristics of insulated windows – Path 3: Table 25c replaces Table 15c

Table 18: Characteristics of the North wall (Case ET110A2)

(Net inside surface area = 7.1494 m²)

| Material | d Thickness [m] | k Conductivity [W/m.K] | Density [kg/m3] | Cp Specific heat [J/kg.K] |
| --- | --- | --- | --- | --- |
| Wallpaper | 0.001 | 0.14 | 700 | 1340 |
| Plasterboard | 0.013 | 0.35 | 850 | 800 |
| Air / Honeycomb Cardboard | 0.046 | 0.307 | 26.1 | 1340 |
| Plasterboard | 0.013 | 0.35 | 850 | 800 |
| Wallpaper | 0.001 | 0.14 | 700 | 1340 |
| Styrodur | 0.060 | 0.032 a | 18 | 1200 |

a. Catalog value replacing imputed value from Case ET110A1.

Table 19: Characteristics of the East wall (Case ET110A2)

(Net inside surface area = 10.1378 m²)

| Material | d Thickness [m] | k Conductivity [W/m.K] | Density [kg/m3] | Cp Specific heat [J/kg.K] |
| --- | --- | --- | --- | --- |
| Wallpaper | 0.001 | 0.14 | 700 | 1340 |
| Plasterboard | 0.010 | 0.35 | 850 | 800 |
| Polystyrene | 0.080 | 0.043 a | 15 | 1200 |
| Air gap | 0.010 | 0.070 | 1.2 | 1000 |
| Hollow block | 0.200 | 1.052 | 1200 | 950 |
| Facing | 0.020 | 1.15 | 1950 | 850 |

a. Catalog value replacing imputed value from Case ET110A1.

Table 20: Characteristics of the South wall (Case ET110A2)

(Net inside surface area = 7.1752 m²)

| Material | d Thickness [m] | k Conductivity [W/m.K] | Density [kg/m3] | Cp Specific heat [J/kg.K] |
| --- | --- | --- | --- | --- |
| Wallpaper | 0.001 | 0.14 | 700 | 1340 |
| Plasterboard | 0.010 | 0.35 | 850 | 800 |
| Polystyrene | 0.080 | 0.043 a | 15 | 1200 |
| Air gap | 0.010 | 0.070 | 1.2 | 1000 |
| Hollow block | 0.200 | 1.052 | 1200 | 950 |
| Facing | 0.020 | 1.15 | 1950 | 850 |

a. Catalog value replacing imputed value from Case ET110A1.

Table 21: Characteristics of the West wall (Case ET110A2)

(Net inside surface area = 11.9401 m²)

| Material | d Thickness [m] | k Conductivity [W/m.K] | Density [kg/m3] | Cp Specific heat [J/kg.K] |
| --- | --- | --- | --- | --- |
| Wallpaper | 0.001 | 0.14 | 700 | 1340 |
| Plasterboard | 0.010 | 0.35 | 850 | 800 |
| Polystyrene | 0.080 | 0.043 a | 15 | 1200 |
| Air gap | 0.010 | 0.070 | 1.2 | 1000 |
| Hollow block | 0.200 | 1.052 | 1200 | 950 |
| Air gap | 0.010 | 0.070 | 1.2 | 1000 |
| Polystyrene | 0.080 | 0.043 a | 15 | 1200 |
| Plasterboard | 0.010 | 0.35 | 850 | 800 |
| Wallpaper | 0.001 | 0.14 | 700 | 1340 |

a. Catalog value replacing imputed value from Case ET110A1.

Table 22a: Characteristics of the ceiling – Path 1 (Case ET110A2)

(Net inside surface area = 14.4025 m²)

| Material | d Thickness [m] | k Conductivity [W/mK] | ρ Density [kg/m3] | Cp Specific heat [J/kgK] |
| --- | --- | --- | --- | --- |
| Wallpaper | 0.001 | 0.14 | 700 | 1340 |
| Plasterboard | 0.013 | 0.35 | 850 | 800 |
| Glass wool 1 | 0.200 | 0.042 a | 11 | 800 |
| Air gap | 0.100 | 0.618 | 1.2 | 1000 |
| Particle board | 0.021 | 0.17 | 700 | 1200 |

a. Catalog value replacing imputed value from Case ET110A1.

Table 22b: Characteristics of the ceiling – Path 2 (Case ET110A2)

(Net inside surface area = 1.8900 m²)

| Material | d Thickness [m] | k Conductivity [W/mK] | ρ Density [kg/m3] | Cp Specific heat [J/kgK] |
| --- | --- | --- | --- | --- |
| Wallpaper | 0.001 | 0.14 | 700 | 1340 |
| Plasterboard | 0.013 | 0.35 | 850 | 800 |
| Glass wool 2 | 0.150 | 0.042 a | 11 | 800 |
| Planks | 0.150 | 0.15 | 500 | 1200 |
| Particle board | 0.021 | 0.17 | 700 | 1200 |

a. Catalog value replacing imputed value from Case ET110A1.

Table 23a: Characteristics of the floor – Path 1 (Case ET110A2)

(Net inside surface area = 13.3525 m²)

| Material | d Thickness [m] | k Conductivity [W/mK] | Density [kg/m3] | Cp Specific heat [J/kgK] |
| --- | --- | --- | --- | --- |
| Ceramic Tile | 0.006 | 1.75 | 2177 | 920 |
| Glue Cement | 0.003 | 1.50 | 1900 | 840 |
| Concrete | 0.008 | 1.75 | 2177 | 920 |
| Concrete + Tubes + Polysty Ribs | 0.016 | 1.47 | 1813 | 954 |
| Polystyrene 1 | 0.035 | 0.040 a | 16 | 1200 |
| Plastic Lining | 0.002 | 0.124 | 265 | 1170 |
| Concrete Slab | 0.065 | 1.75 | 2200 | 950 |
| Insulated Block 1 | 0.070 | 0.040 a | 18 | 1200 |
| Insulated Block 2 | 0.050 | 0.040 a | 18 | 1200 |
| Polystyrene 2 | 0.030 | 0.040 a | 18 | 1200 |
| Plasterboard | 0.013 | 0.35 | 850 | 800 |

a. Catalog value replacing imputed value from Case ET110A1.

Table 23b: Characteristics of the floor – Path 2 (Case ET110A2)

(Net inside surface area = 1.4700 m²)

| Material | d Thickness [m] | k Conductivity [W/mK] | Density [kg/m3] | Cp Specific heat [J/kgK] |
| --- | --- | --- | --- | --- |
| Ceramic Tile | 0.006 | 1.75 | 2177 | 920 |
| Glue Cement | 0.003 | 1.50 | 1900 | 840 |
| Concrete | 0.008 | 1.75 | 2177 | 920 |
| Concrete + Tubes + Polysty Ribs | 0.016 | 1.47 | 1813 | 954 |
| Polystyrene 1 | 0.035 | 0.040 a | 16 | 1200 |
| Plastic Lining | 0.002 | 0.124 | 265 | 1170 |
| Concrete Slab | 0.065 | 1.75 | 2200 | 950 |
| Insulated Block 1 | 0.070 | 0.040 a | 18 | 1200 |
| Concrete Beam 2 | 0.050 | 1.75 | 2200 | 950 |
| Polystyrene 2 | 0.030 | 0.040 a | 18 | 1200 |
| Plasterboard | 0.013 | 0.35 | 850 | 800 |

a. Catalog value replacing imputed value from Case ET110A1.

Table 23c: Characteristics of the floor – Path 3 (Case ET110A2)

(Net inside surface area = 1.4700 m²)

| Material | d Thickness [m] | k Conductivity [W/mK] | Density [kg/m3] | Cp Specific heat [J/kgK] |
| --- | --- | --- | --- | --- |
| Ceramic Tile | 0.006 | 1.75 | 2177 | 920 |
| Glue Cement | 0.003 | 1.50 | 1900 | 840 |
| Concrete | 0.008 | 1.75 | 2177 | 920 |
| Concrete + Tubes + Polysty Ribs a | 0.016 | 1.47 | 1813 | 954 |
| Polystyrene 1 | 0.035 | 0.040 a | 16 | 1200 |
| Plastic Lining | 0.002 | 0.124 | 265 | 1170 |
| Concrete Slab | 0.065 | 1.75 | 2200 | 950 |
| Concrete Beam 1 | 0.070 | 1.75 | 2200 | 950 |
| Concrete Beam 2 | 0.050 | 1.75 | 2200 | 950 |
| Polystyrene 2 | 0.030 | 0.040 a | 18 | 1200 |
| Plasterboard | 0.013 | 0.35 | 850 | 800 |

a. Catalog value replacing imputed value from Case ET110A1.

Table 24: Characteristics of the door (Case ET110A2)

(Net inside surface area = 1.8281 m²)

| Material | d Thickness [m] | k Conductivity [W/m.K] | Density [kg/m3] | Cp Specific heat [J/kg.K] |
| --- | --- | --- | --- | --- |
| Blended Wood/Air/Cardboard + Plywood + Plexiglass | 0.036 | 0.093 a | 307 | 1317 |
| Blended Air Gap | 0.038 | 0.254 | 1.2 | 1000 |
| Styrodur (see Figure 14) | 0.060 | 0.032 a | 18 | 1200 |

a. Catalog value replacing imputed value from Case ET110A1.

Table 25a: Characteristics of insulated windows – Path 1 (Case ET110A2)

(Net inside surface area = 0.9905 m²)

| Material | d Thickness [m] | k Conductivity [W/m.K] | Density [kg/m3] | Cp Specific heat [J/kg.K] |
| --- | --- | --- | --- | --- |
| Blended Glass/Air Gap /Glass | 0.020 | 0.124 | 1081 | 900 |
| Air Gap | 0.009 | 0.062 a | 1.2 | 1000 |
| Glasswool 1 | 0.200 | 0.033 a | 11 | 800 |
| Polystyrene 1 | 0.070 | 0.033 a | 16 | 1200 |

a. Catalog value replacing imputed value from Case ET110A1.

Table 25b: Characteristics of insulated windows – Path 2 (Case ET110A2)

(Net inside surface area = 0.1385 m²)

| Material | d Thickness [m] | k Conductivity [W/m.K] | Density [kg/m3] | Cp Specific heat [J/kg.K] |
| --- | --- | --- | --- | --- |
| PVC | 0.062 | 0.16 | 1380 | 1000 |
| Glasswool 2 | 0.188 | 0.033 a | 11 | 800 |
| Polystyrene 1 | 0.070 | 0.033 a | 16 | 1200 |

a. Catalog value replacing imputed value from Case ET110A1.

Table 25c: Characteristics of insulated windows – Path 3 (Case ET110A2)

(Net inside surface area = 0.6734 m²)

| Material | d Thickness [m] | k Conductivity [W/m.K] | Density [kg/m3] | Cp Specific heat [J/kg.K] |
| --- | --- | --- | --- | --- |
| Blended PVC + facing + plasterboard b | 0.062 | 0.267 a | 1442 | 975 |
| Glasswool 3 c | 0.188 | 0.208 a | 316 | 808 |
| Polystyrene 2 c | 0.070 | 0.208 a | 320 | 1145 |

a. Catalog value replacing imputed value from Case ET110A1.

b. As a modeling simplification, the Path-3 window frame material includes the external setback cavity facing (known thermal bridge) and the plasterboard covering the facing on the test cell interior surface; see Appendix C for supporting information.

c. As a modeling simplification, the Glasswool 3 and Polystyrene 2 materials include the external setback cavity facing (known thermal bridge); see Appendix C for supporting information.

#### Infiltration

2.2.2.5.1  For Case ET110A2, infiltration shall be:

- 0.05775 ACH

2.2.2.5.2  The model shall assume test cell infiltration air exchange is distributed equally with each guard zone; i.e., 1/6 of the total infiltration rate selected from the range above is attributed to each guard zone.

2.2.2.5.3  Informative Notes

1. The given infiltration ACH is an average based on two tracer-gas measurements as follows:

- 0.0265 ACH was measured about 6 weeks before running the test case

- 0.089 ACH (likely worst case) was measured about 6 months after running the test case and after test cell reconfigurations for other experiments not related to this empirical validation work; this leakier rate was found to be fixable (decreased to 0.020 ACH) after fixing leaks in the Cell A north door.

2. The range of infiltration ACH gives an equivalent range of UA attributable to infiltration (UAinf) of:

- UAinf = 0.37 to 1.25 W/K (0.81 W/K average)

3. For supporting information, see Appendix C, Table C-1.

### Case ET110B1: Artificial Climate, Steady-State Overall Building Loss Coefficient with Insulated Windows, Cell B, Applying Specified Catalog Material Properties Except for Selected Imputed Insulation Conductivities

#### Informative Note: Objective and Method of the Test Case

Case ET110B1, applying Cell B, is specified as an extension case based on the Cell A artificial climate base case (Case ET110A1).

As specified below, Cell B is constructed as a twin of Cell A except its East and West walls are juxtaposed versus Cell A, and Cell B has different imputed conductivities than Cell A based on different measured wall UA values. Cell B also has different test cell input and guard zone temperature data versus Cell A. Twin test cells are most useful for testing the ability to model sensitivities in the natural climate configuration. Therefore, it is necessary to characterize Cell B in parallel with Cell A, as shown in this test specification.

Similarly as Cell A (Case ET110A1), guard-zone temperatures were set to approximately Tguards = 10˚C and test cell temperature set to TcellB = 35 ˚C. See data files listed in Section 2.2.3.3 for guard zone and test cell hourly temperatures (set points). For an idealized heating system (that effectively outputs building load), apply results comparisons as listed with Objectives and Methods for Case ET110A1; see Section 2.2.1.1 Informative Notes, Item 3.

#### Extension Case Basis

Case ET110B1 shall be modeled exactly the same as Case ET110A1 except for changes detailed in the following sections.

2.2.3.3 Test Cell Conditions and Guard-Zone Temperatures

##### 2.2.3.3.1	Test Cell Measured Data and Weather Input Data

Hourly data files and the test data sets durations for Case ET110B1 are listed in Table 26. These data files are included with the accompanying electronic media; also see Readme-ET100series-Files.docx there. The data files apply the same conventions as Case ET110A1; see Section 2.2.1.3.1.

The ET110B-Measurements-GMT+1-mmddyy.csv hourly data format is given in Table 27. The header labels of Table 27 apply similarly as those for Table 3 (see Section 2.2.1.3.1), except “Usage” category “Output” (only for data labeled “Qhtr”) relates to the requirements of Section 2.2.3.4.

Table 26 Primary Data File Directory (Case ET110B1)

| File Name | Data Type | Time Step | Data Duration (“MM/DD/YYYY hh”) |
| --- | --- | --- | --- |
| ET110B-Measurements-GMT+1.csv d | Test Cell B | Hour | 01/26/2000 12 through 02/11/2000 09 |
| ET110meteoGMT+1_within_Melun-071530_MY.2000.epw a,b,c,d | Local ETNA weather inserted within Melun, France AMY data | Hour | 01/01/2000 01 through 12/31/2000 24 |

a. Informative Note: This is the same weather data provided for Case ET110A1.

b. Informative Note: Epw format is described at: http://climate.onebuilding.org/papers/EnergyPlus_Weather_File_Format.pdf.

c. Informative Note: In the artificial climate cases, for programs that model guard zones as boundary conditions applied to each test cell wall rather than as literal zones, the weather data is essentially dummy data – i.e., not used in the model other than to satisfy the requirement of most BPS software to have a weather data set.

d. Informative Note: For further supporting information regarding these data files, see Readme-ET100series-Files.docx and also Neymark et al. (2004).

Table 27 Cell B Hourly Data Format

| Column | Label | Usage | Description | Units |
| --- | --- | --- | --- | --- |
| A | Date | Input | Date and time in format “MM/DD/YYYY hh:mm” (preceding hour format, e.g., Hour 10:00 = 09:00-10:00) |  |
| B | Tattic | Input | Attic air temperature a | ºC |
| C | Tcellar | Input | Cellar air temperature a | ºC |
| D | Tnorth | Input | North guard air temperature a | ºC |
| E | Teast | Input | East guard air temperature a | ºC |
| F | Tsouth | Input | South guard air temperature a | ºC |
| G | Twest | Input | West guard air temperature a | ºC |
| H | Tcell | Input | Test cell setpoint temperature a | ºC |
| I | Qfan | Input | Fan energy | Wh |
| J | HWDsafr | Input | Fan supply airflow rate | m3/h |
| K | Qhtr | Output | Heater energy | Wh |

a. See Figure 16 (Section 2.2.3.5.1) and Figures 6 and 8 (Section 2.2.1.7.1.3) for location of Cell B guard zones.

Informative Notes:

- Within the .csv file each line contains data for one hour, and the first four lines include column labels and units.

- Cell B air (setpoint) temperature sensor locations are given in Neymark et al. (2004), Figure 18 (Section 2.2.1.7.2). Guard zone temperature sensors were located centrally to represent average guard zone temperatures; the precise locations were not documented.

2.2.3.4	Output Requirements.

Provide output applying tab ET110B1 of the template ET100series-output-GMT+1….xlsx, included with the accompanying electronic media. The following requirements shall apply:

- Table 2.2.3-3(28) lists required and optional hourly-integrated-average outputs. Informative Note: The only differences in this table versus Table 5 is that the Cell B east wall, which has no window, requires flux output for only one 1-D conduction path and the Cell B west wall with window requires flux output for four 1-D conduction paths. The sequence of wall inside surface flux output entry remains as ceiling, floor, then north, east, south, and west walls.

- Output shall be provided for the same simulation duration time period indicated in Section 2.2.1.5 (Case ET110A1).

- Sections 2.2.1.6(c) and (d) (Case ET110A1), regarding preceding hour time convention and not making changes to the output template, shall also apply.

2.2.3.4.1 Inside Surface Flux Output

For software applying the 16 alternative 1-D conduction paths specified in Section 2.2.3.6.1.2 and related subsections of Section 2.2.3.6.3.2, this output (see Table 2.2.3-3(28)) shall be provided as allowed by the software being tested. This output corresponds with each 1-D conduction path specified for Cell B in Section 2.2.3.6.3.2. Inside surface convective, radiative, and combined convective and radiative fluxes are defined in Sections 2.2.1.6.1.1, 2.2.1.6.1.2, and 2.2.1.6.1.3, respectively (Case ET110A1). Informative Note: This diagnostic output is provided to check modeling of individual 1-D conduction paths.

2.2.3.4.2 Output Format

The output format of Section 2.2.1.6.2 (Case ET110A1) shall apply, except the “Usage” categories of Table 2.2.3-3(28) apply section references specific to this test case as follows:

- “Input Check” data shall be applied for checking “input” data to the software being tested (see Section 2.2.3.3.1)

- “Required Output” (only for data labeled “Qhtr”) shall be applied for comparison with the provided “output” measured heating energy (see Section 2.2.3.3.1)

- “Optional Output” shall be allowed for comparison with the provided measurement-based individual surface heat flow output (see Section 2.2.3.4.3), for software applying the 16 alternative 1-D conduction paths specified for this test case.

  - Informative Note: This output may be provided if the software being tested allows this output or a subset of this output.

- Table 2.2.3-3(28).  Cell B Hourly Output File Format

| Column | Label | Usage | Description | Units |
| --- | --- | --- | --- | --- |
| A | Date | Input Check | Date and time in format “MM-DD-YYYY hh:mm” (preceding hour format, e.g., Hour 10:00 = 09:00-10:00) |  |
| B | Tattic | Input Check | Attic air temperature | ºC |
| C | Tcellar | Input Check | Cellar air temperature | ºC |
| D | Tnorth | Input Check | North guard air temperature | ºC |
| E | Teast | Input Check | East guard air temperature | ºC |
| F | Tsouth | Input Check | South guard air temperature | ºC |
| G | Twest | Input Check | West guard air temperature | ºC |
| H | Tcell | Input Check | Test cell air temperature | ºC |
| I | Qfan | Input Check | Fan energy consumption | Wh |
| J | HWDsafr | Input Check | Supply air flow rate | m3/h |
| K | Qhtr | Required Output | Heater energy consumption | Wh |
| L | q,c1,conv | Optional Output | Ceiling Path 1 inside surface convective flux a | Wh/m2 |
| M | q,c1,rad | Optional Output | Ceiling Path 1 inside surface radiative flux a | Wh/m2 |
| N | q,c1,tot | Optional Output | Ceiling Path 1 inside surface total convective and radiative flux a | Wh/m2 |
| O | q,c2,conv | Optional Output | Ceiling Path 2 inside surface convective flux a | Wh/m2 |
| P | q,c2,rad | Optional Output | Ceiling Path 2 inside surface radiative flux a | Wh/m2 |
| Q | q,c2,tot | Optional Output | Ceiling Path 2 inside surface total convective and radiative flux a | Wh/m2 |
| R | q,f1,conv | Optional Output | Floor Path 1 inside surface convective flux a | Wh/m2 |
| S | q,f1,rad | Optional Output | Floor Path 1 inside surface radiative flux a | Wh/m2 |
| T | q,f1,tot | Optional Output | Floor Path 1 inside surface total convective and radiative flux a | Wh/m2 |
| U | q,f2,conv | Optional Output | Floor Path 2 inside surface convective flux a | Wh/m2 |
| V | q,f2,rad | Optional Output | Floor Path 2 inside surface radiative flux a | Wh/m2 |
| W | q,f2,tot | Optional Output | Floor Path 2 inside surface total convective and radiative flux a | Wh/m2 |
| X | q,f3,conv | Optional Output | Floor Path 3 inside surface convective flux a | Wh/m2 |
| Y | q,f3,rad | Optional Output | Floor Path 3 inside surface radiative flux a | Wh/m2 |
| Z | q,f3,tot | Optional Output | Floor Path 3 inside surface total convective and radiative flux a | Wh/m2 |
| AA | q,n,conv | Optional Output | North wall inside surface convective flux a | Wh/m2 |
| AB | q,n,rad | Optional Output | North wall inside surface radiative flux a | Wh/m2 |
| AC | q,n,tot | Optional Output | North wall inside surface total convective and radiative flux a | Wh/m2 |
| AD | q,d,conv | Optional Output | Door inside surface convective flux a | Wh/m2 |
| AE | q,d,rad | Optional Output | Door inside surface radiative flux a | Wh/m2 |
| AF | q,d,tot | Optional Output | Door inside surface total convective and radiative flux a | Wh/m2 |
| AG | q,e,conv | Optional Output | East wall inside surface convective flux a | Wh/m2 |
| AH | q,e,rad | Optional Output | East wall inside surface radiative flux a | Wh/m2 |
| AI | q,e,tot | Optional Output | East wall inside surface total convective and radiative flux a | Wh/m2 |
| AJ | q,s,conv | Optional Output | South wall inside surface convective flux a | Wh/m2 |
| AK | q,s,rad | Optional Output | South wall inside surface radiative flux a | Wh/m2 |
| AL | q,s,tot | Optional Output | South wall inside surface total convective and radiative flux a | Wh/m2 |
| AM | q,swin1,conv | Optional Output | South window Path 1 inside surface convective flux a | Wh/m2 |
| AN | q,swin1,rad | Optional Output | South window Path 1 inside surface radiative flux a | Wh/m2 |
| AO | q,swin1,tot | Optional Output | South window Path 1 surface total convective & radiative flux a | Wh/m2 |
| AP | q,swin2,conv | Optional Output | South window Path 2 inside surface convective flux a | Wh/m2 |
| AQ | q,swin2,rad | Optional Output | South window Path 2 inside surface radiative flux a | Wh/m2 |
| AR | q,swin2,tot | Optional Output | South window Path 2 surface total convective & radiative flux a | Wh/m2 |
| AS | q,swin3,conv | Optional Output | South window Path 3 inside surface convective flux a | Wh/m2 |
| AT | q,swin3,rad | Optional Output | South window Path 3 inside surface radiative flux a | Wh/m2 |
| AU | q,swin3,tot | Optional Output | South window Path 3 surface total convective & radiative flux a | Wh/m2 |
| AV | q,w,conv | Optional Output | West wall inside surface convective flux a | Wh/m2 |
| AW | q,w,rad | Optional Output | West wall inside surface radiative flux a | Wh/m2 |
| AX | q,w,tot | Optional Output | West wall inside surface total convective and radiative flux a | Wh/m2 |
| AY | q, wwin1,conv | Optional Output | West window Path 1 inside surface convective flux a | Wh/m2 |
| AZ | q,wwin1,rad | Optional Output | West window Path 1 inside surface radiative flux a | Wh/m2 |
| BA | q,wwin1,tot | Optional Output | West window Path 1 surface total convective & radiative flux a | Wh/m2 |
| BB | q,wwin2,conv | Optional Output | West window Path 2 inside surface convective flux a | Wh/m2 |
| BC | q,wwin2,rad | Optional Output | West window Path 2 inside surface radiative flux a | Wh/m2 |
| BD | q,wwin2,tot | Optional Output | West window Path 2 surface total convective and radiative flux a | Wh/m2 |
| BE | q,wwin3,conv | Optional Output | West window Path 3 inside surface convective flux a | Wh/m2 |
| BF | q,wwin3,rad | Optional Output | West window Path 3 inside surface radiative flux a | Wh/m2 |
| BG | q,wwin3,tot | Optional Output | West window Path 3 surface total convective and radiative flux a | Wh/m2 |

a. See Section 2.2.1.6.1.

##### 2.2.3.4.3  Comparing Software Output to Measured Data and Empirical Values Derived from Measured Data

Results comparisons shall be applied only for the given best steady-state period of the data; see Section 2.2.3.4.3.1.

The following measured data are provided for results comparisons for all models:

- Heater energy (Qhtr): see Section 2.2.3.4.3.2

The following empirical values derived from measured data are provided for software applying the 16 alternative 1-D conduction paths specified for this test case:

- Total surface heat fluxes (q,x,tot) for each conduction path (x): see Section 2.2.3.4.3.3

Informative Note: This is the same comparison method as in Case ET110A1, except references to sections, tables, and accompanying files are specific to this test case.

2.2.3.4.3.1 Application of Best Steady-State Data

For Case ET110B1, the best steady-state time period is:

2/10/2000 16:00 to 2/11/2000 9:00, GMT+1

(The time interval applies “MM/DD/YYYY hh:mm” format and preceding hour interval time convention of Section 2.1.1)

Informative Notes:

- This is the same best steady-state time period as in Case ET110A1.

- Determination of the best steady-state period for a given test case is described in Appendix C.

2.2.3.4.3.2 Comparison of Required Heater Energy (Qhtr) Results

The primary results comparison is for Qhtr provided in ET110B-Measurements-GMT+1.csv (see Section 2.2.3.3.1), corresponding with the best steady-state period (last 18 rows of the csv file).

Informative Note: If the program has input the test case correctly, for steady-state output it is reasonable to expect modeled hourly output Qhtr during the best steady-state period that is mostly within averaged measured Qhtr ± u(Q), Here, u(Q) is ± 1.5%[tk] for a 2-sigma (95% confidence interval) uncertainty band.

2.2.3.4.3.3 Comparison of Optional Inside Surface Flux Results

For software applying the 16 alternative 1-D conduction paths specified for this test case, total surface fluxes (q,x,tot) derived from measurements are provided in the file ET100series-MeasBasedSurfFlux-GMT+1.xlsx, see tab ‘ET110B’. Format of this file is provided in Table 2.2.3-3a(28a).

For the purpose of this comparison, data is only provided for the best steady-state period; see the last 18 rows of ET100series-MeasBasedSurfFlux-GMT+1.xlsx, tab ‘ET110B’.

Informative Notes:

- These fluxes are provided for the purpose of comparing best-steady-state-period modeled individual conduction-path inside surface fluxes to measurement-based individual conduction-path heat fluxes derived from empirical measurements.

- At steady state, modeled total inside surface fluxes and measurement-based individual conduction-path heat fluxes should be approximately equal.

- Derivation of hourly q,x,tot at best steady-state is provided in ET100series-MeasBasedSurfFlux-GMT+1.xlsx, tab ‘ET110B-SurfFluxDeriv’. Determination of measured UA values applied for this derivation is described in Appendix C.

- Table 2.2.3-3a(28a).  Cell B Hourly Measurement-Based Heat-Flux File Format

| Column | Label | Description | Units |
| --- | --- | --- | --- |
| A | Date | Date and time in format “MM-DD-YYYY hh:mm” (preceding hour format, e.g., Hour 10:00 = 09:00-10:00) |  |
| B | q,c1,tot | Ceiling Path 1 | Wh/m2 |
| C | q,c2,tot | Ceiling Path 2 | Wh/m2 |
| D | q,f1,tot | Floor Path 1 | Wh/m2 |
| E | q,f2,tot | Floor Path 2 | Wh/m2 |
| F | q,f3,tot | Floor Path 3 | Wh/m2 |
| G | q,n,tot | North wall | Wh/m2 |
| H | q,d,tot | Door | Wh/m2 |
| I | q,e,tot | East wall | Wh/m2 |
| J | q,s,tot | South wall | Wh/m2 |
| K | q,swin1,tot | South window Path 1 | Wh/m2 |
| L | q,swin2,tot | South window Path 2 | Wh/m2 |
| M | q,swin3,tot | South window Path 3 | Wh/m2 |
| N | q,w,tot | West wall | Wh/m2 |
| O | q,wwin1,tot | West window Path 1 | Wh/m2 |
| P | q,wwin2,tot | West window Path 2 | Wh/m2 |
| Q | q,wwin3,tot | West window Path 3 | Wh/m2 |

2.2.3.5	Geometry.

Cell B shall be exactly the same as Cell A, except as described in the following sections.

Two options for modeling guard zones are specified depending on the capabilities of the tested programs:

- guard zones modeled as boundary conditions on the exterior side of each test cell bounding surface (Section 2.2.3.5.1)

- guard zones modeled as separate zones adjacent to the test cell bounding surfaces (Section 2.2.3.5.3).

2.2.3.5.1  Summary geometry for models applying guard zones as boundary conditions

For programs that require modeling the guard zones as actual physical zones, see the instructions of Sections 2.2.3.5.2 and 2.2.3.5.3, and skip the remainder of this section.

As shown in Figure 16, the building is oriented 30° E of North, so that the test cell bounding surface that would nominally be called the "South” wall is oriented at 30° West of South, and the other walls are oriented and named accordingly with orientations offset 30° from their nominal cardinal directions. Informative Note: This is the same orientation as Cell A.

Figure 16 also shows the plan view and a sectional view of Cell B and indicates the names of its six guard zones. These names are associated with hourly data identifiers within the accompanying file ET110B-GMT+1.csv (see previous Section 2.2.3.3.1); e.g., “Tsouth” designates the south guard zone temperature data provided in column F of the file.

Other information for defining the guard zones as boundary conditions, related to surface heat transfer and additional supporting data, are provided in Sections 2.2.3.8 (Surface Heat Transfer) and 2.2.3.11 (Thermal Guards).

Cell B

Cell B

N

Elevation Section View (looking 30° south of east through page)

Plan View

Figure 16: ETNA Cell B, Summary Diagrams with Artificial-Climate Thermal Guards

Note 1: Cell B internal dimension details are provided in Figure 17.

Note 2: Attic and cellar also fully cover ceiling and floor, respectively, of Cell B and east guard.

2.2.3.5.2	Test cell detailed geometry

Cell B shall be exactly the same as Cell A, except the east and west walls are juxtaposed applying the following:

- Section 2.2.3.5.2.1 replaces Section 2.2.1.7.1.2.1 (primary inside surfaces)

- Section 2.2.3.5.2.2 (west wall and window) replaces Section 2.2.1.7.1.2.4 (east wall and window)

- Section 2.2.3.5.2.3 replaces Section 2.2.1.7.1.2.6 (surface area summary)

All other Cell B geometry is the same as for Cell A.

2.2.3.5.2.1	Cell B primary inside surfaces

Cell B shall be exactly the same as Cell A, except the east and west walls are juxtaposed

Figure 17 specifies the inside-surface (interior) dimensions of Cell B.   Interior surface dimensions for the east wall, floor, and ceiling are taken directly from this figure.

East Wall

Figure 17 Inside-Surface Dimensions of Cell B

Note: Ceiling is at 2.565 m height, parallel to floor, with same dimensions as floor.

2.2.3.5.2.2  West wall and window

Figure 18 specifies the west wall geometry as viewed from the exterior, including the position of the window in the west wall and the dimensions of the window glazing panels and framework. Informative Notes:

1. This is the same geometry as for the Cell A east wall, except the dimensions that define the horizontal position of the window within the west wall have been juxtaposed.

2. As the west wall is guarded in both artificial and natural climate cases, the exact position of the window within the wall should not affect the results.

3. In cases with insulation applied externally to windows, such as Case ET110B1, the windows may be modeled as walls, or subsections of walls, because with window insulation in place (see Section 2.2.1.7.2.9) there is no transmitted solar radiation.

Figure 18: Dimensioned west wall with window elevation, exterior view

2.2.3.5.2.3  Surface area summary.

The Cell B component surfaces areas shall be the same as for Cell A except the east and west walls are exchanged as shown in Table 28. This table indicates the component surface areas for the Cell B west wall, along with overall total areas for the west and east walls. This table also includes the sub-areas for the five alternative 1-D conduction paths that are exchanged shown in bold font; these are defined with the construction details of Section 2.2.3.6, as summarized in Section 2.2.3.6.1.2. See Table 6 (Section 2.2.1.7.1.2.6) for component surface areas for the floor, ceiling, north wall, and south wall.

Informative Note: This table is intended for checking geometry inputs by comparing tested-program intermediate geometry output with this table.

Table 28 Cell B Boundary-Surface Areas a,b

a. Sub-areas for the five alternative 1-D conduction paths defined in Section 2.2.3.6 for the Cell B west and east walls.

b. Author Note[tk]: Source file = “Surface Area Check (080423).xlsx” in “\SupplementaryFiles”, not included with accompanying files.

2.2.3.5.3  Alternative geometry for programs that require physically defining the guard zones

Users that apply guard zones as boundary conditions (per Section 2.2.3.5.1) in place of physically defining guard zone geometry and material constructions shall skip this section and continue with Section 2.2.3.6.

Users with programs that require physically defining the guard zones shall apply the instructions of Section 2.2.1.7.1.3 (Case ET110A1) and apply guard zone geometry to Cell B as shown in Figures 6 through 8 there. In Figure 7, the dimensions depicted for Cell A and its guard zones are the same for Cell B, except the “East Guard” of Cell A becomes the “West Guard” (see the note with Figure 7).

Figures 6 through 8 also indicate the names of each guard zone. These names are associated with hourly data identifiers within the accompanying file ET110B-GMT+1.csv (see previous Section 2.2.3.3.1); e.g., “Tsouth” designates the south guard zone temperature data provided in column F of the file.

2.2.3.6	Test Cell Bounding Surface Material Constructions.

The following sections specify material constructions of the test cell bounding surfaces and subsurfaces:

- Construction modeling options (Section 2.2.3.6.1)

- Required characteristics (Section 2.2.3.6.2)

- Alternative construction properties tables (Section 2.2.3.6.3)

###### 2.2.3.6.1 Construction Modeling Options

In the following sections for each bounding surface, construction specifications are presented as required characteristics and alternative construction specifications.

2.2.3.6.1.1 Required characteristics include:

- Empirically determined UA values

- Construction details, as shown in the figures.

2.2.3.6.1.2 Alternative construction specifications consist of material properties tables that include:

- Catalog values

- Imputed thermal conductivities for selected material layers; imputed values are highlighted in yellow.

- 16 parallel 1-D conduction paths applied for determining the imputed thermal conductivities.

Informative Notes:

- Material property tables in the following sections are intended for simulations applying 1-dimensional thermal diffusion models, and are derived based on the interior surface area of a given bounding surface.

- Imputed properties are only valid for the given conduction paths.

- The alternative construction specifications are recommended for use based on Section 2.1.10.

Informative Appendix C describes calculation of imputed values.

###### 2.2.3.6.2 Required Characteristics

Table 29 specifies UA values and cross-references required geometry and construction figures for each wall.

For modelers requiring further guidance to specify inputs of material properties, apply the alternative construction specification of Section 2.2.3.6.3 (following). Informative Note: Use of the Section 2.2.3.6.3 alternative is recommended (see Section 2.1.10).

Table 29 Cell B Required Characteristics (Case ET110B1)

| Wall | UA Value, W/K | Geometry Figure | Construction Figure |
| --- | --- | --- | --- |
| North | 5.70 | Figure 5 b (Section 2.2.1.7.1.2.5) | Figure 9 b (Section 2.2.1.7.2.2.1) |
| East a | 3.02 | Figure 17 (Section 2.2.3.5.2.1) | Figure 11 a (Section 2.2.1.7.2.5.1) |
| South | 8.68 | Figure 3 b (Section 2.2.1.7.1.2.2) | Figure 10 b (Section 2.2.1.7.2.3.1) |
| West a | 8.94 | Figure 18 (Section 2.2.3.5.2.2) | Figure 10 a (Section 2.2.1.7.2.3.1) |
| Ceiling | 2.52 | Figure 17 c (Section 2.2.3.5.2.1) | Figure 12a b (Section 2.2.1.7.2.6.1) |
| Floor | 7.28 | Figure 17 c (Section 2.2.3.5.2.1) | Figure 13a b (Section 2.2.1.7.2.7.1) |
| Door | Included with North wall | Figure 5 b (Section 2.2.1.7.1.2.5) | Figure 14a b (Section 2.2.1.7.2.8.1) |
| Window Insulation Module | Reduces west and south walls each by 2.44 W/K | Figure 3 b Figure 18 | Figure 15a b (Section 2.2.1.7.2.9.1) |

a. Informative Note: Cell B East and West walls are juxtaposed versus Cell A.

b. Informative Note: Same figure as for Cell A.

c. Informative Note: Ceiling and floor of Cell B have same geometry as Cell A.

###### 2.2.3.6.3 Alternative Construction Specification

2.2.3.6.3.1  If the modeler does not require further guidance to develop inputs as specified in Section 2.2.3.6.2, skip the remaining instructions and proceed to Section 2.2.3.7.

2.2.3.6.3.2  Changes shall be made to selected imputed material thermal conductivities specified in Section 2.2.1.7.2 (Case ET110A1); imputed values for Cell B replacing imputed values for Cell A are indicated via footnotes and bold yellow-highlighted text in the following tables:

- Characteristics of the North wall: Table 30 replaces Table 7

- Characteristics of the West wall: Table 31 replaces Table 8 (Cell A East)

- Characteristics of the South wall: Table 32 replaces Table 9

- Characteristics of the East wall: Table 33 replaces Table 10 (Cell A West)

- Characteristics of the ceiling – Path 1: Table 34a replaces Table 11a

- Characteristics of the ceiling – Path 2: Table 34b replaces Table 11b

- Characteristics of the floor – Path 1: Table 35a replaces Table 12a

- Characteristics of the floor – Path 2: Table 35b replaces Table 12b

- Characteristics of the floor – Path 3: Table 35c replaces Table 12c

- Characteristics of the door: Table 36 replaces Table 13

- Characteristics of insulated windows – Path 1: Table 37a replaces Table 15a

- Characteristics of insulated windows – Path 2: Table 37b replaces Table 15b

- Characteristics of insulated windows – Path 3: Table 37c replaces Table 15c

Table 30: Characteristics of the North wall (Case ET110B1)

(Net inside surface area = 7.1494 m²)

| Material | d Thickness [m] | k Conductivity [W/m.K] | Density [kg/m3] | Cp Specific heat [J/kg.K] |
| --- | --- | --- | --- | --- |
| Wallpaper | 0.001 | 0.14 | 700 | 1340 |
| Plasterboard | 0.013 | 0.35 | 850 | 800 |
| Air / Honeycomb Cardboard | 0.046 | 0.307 | 26.1 | 1340 |
| Plasterboard | 0.013 | 0.35 | 850 | 800 |
| Wallpaper | 0.001 | 0.14 | 700 | 1340 |
| Styrodur | 0.060 | 0.0518 a | 18 | 1200 |

a.  Imputed value for Case ET110B1.

Table 31: Characteristics of the West wall (Case ET110B1)

(Net inside surface area = 10.1378 m²)

| Material | d Thickness [m] | k Conductivity [W/m.K] | Density [kg/m3] | Cp Specific heat [J/kg.K] |
| --- | --- | --- | --- | --- |
| Wallpaper | 0.001 | 0.14 | 700 | 1340 |
| Plasterboard | 0.010 | 0.35 | 850 | 800 |
| Polystyrene | 0.080 | 0.0353 a | 15 | 1200 |
| Air gap | 0.010 | 0.070 | 1.2 | 1000 |
| Hollow block | 0.200 | 1.052 | 1200 | 950 |
| Facing | 0.020 | 1.15 | 1950 | 850 |

a.  Imputed value for Case ET110B1.

Table 32: Characteristics of the South wall (Case ET110B1)

(Net inside surface area = 7.1752 m²)

| Material | d Thickness [m] | k Conductivity [W/m.K] | Density [kg/m3] | Cp Specific heat [J/kg.K] |
| --- | --- | --- | --- | --- |
| Wallpaper | 0.001 | 0.14 | 700 | 1340 |
| Plasterboard | 0.010 | 0.35 | 850 | 800 |
| Polystyrene | 0.080 | 0.0503 a | 15 | 1200 |
| Air gap | 0.010 | 0.070 | 1.2 | 1000 |
| Hollow block | 0.200 | 1.052 | 1200 | 950 |
| Facing | 0.020 | 1.15 | 1950 | 850 |

a.  Imputed value for Case ET110B1.

Table 33: Characteristics of the East wall (Case ET110B1)

(Net inside surface area = 11.9401 m²)

| Material | d Thickness [m] | k Conductivity [W/m.K] | Density [kg/m3] | Cp Specific heat [J/kg.K] |
| --- | --- | --- | --- | --- |
| Wallpaper | 0.001 | 0.14 | 700 | 1340 |
| Plasterboard | 0.010 | 0.35 | 850 | 800 |
| Polystyrene | 0.080 | 0.0505 a | 15 | 1200 |
| Air gap | 0.010 | 0.070 | 1.2 | 1000 |
| Hollow block | 0.200 | 1.052 | 1200 | 950 |
| Air gap | 0.010 | 0.070 | 1.2 | 1000 |
| Polystyrene | 0.080 | 0.0505 a | 15 | 1200 |
| Plasterboard | 0.010 | 0.35 | 850 | 800 |
| Wallpaper | 0.001 | 0.14 | 700 | 1340 |

a.  Imputed value for Case ET110B1.

Table 34a: Characteristics of the ceiling – Path 1 (Case ET110B1)

(Net inside surface area = 14.4025 m²)

| Material | d Thickness [m] | k Conductivity [W/mK] | ρ Density [kg/m3] | Cp Specific heat [J/kgK] |
| --- | --- | --- | --- | --- |
| Wallpaper | 0.001 | 0.14 | 700 | 1340 |
| Plasterboard | 0.013 | 0.35 | 850 | 800 |
| Glass wool 1 | 0.200 | 0.0340 a | 11 | 800 |
| Air gap | 0.100 | 0.618 | 1.2 | 1000 |
| Particle board | 0.021 | 0.17 | 700 | 1200 |

a.  Imputed value for Case ET110B1.

Table 34b: Characteristics of the ceiling – Path 2 (Case ET110B1)

(Net inside surface area = 1.8900 m²)

| Material | d Thickness [m] | k Conductivity [W/mK] | ρ Density [kg/m3] | Cp Specific heat [J/kgK] |
| --- | --- | --- | --- | --- |
| Wallpaper | 0.001 | 0.14 | 700 | 1340 |
| Plasterboard | 0.013 | 0.35 | 850 | 800 |
| Glass wool 2 | 0.150 | 0.0340 a | 11 | 800 |
| Planks | 0.150 | 0.15 | 500 | 1200 |
| Particle board | 0.021 | 0.17 | 700 | 1200 |

a.  Imputed value for Case ET110B1.

Table 35a: Characteristics of the floor – Path 1 (Case ET110B1)

(Net inside surface area = 13.3525 m²)

| Material | d Thickness [m] | k Conductivity [W/mK] | Density [kg/m3] | Cp Specific heat [J/kgK] |
| --- | --- | --- | --- | --- |
| Ceramic Tile | 0.006 | 1.75 | 2177 | 920 |
| Glue Cement | 0.003 | 1.50 | 1900 | 840 |
| Concrete | 0.008 | 1.75 | 2177 | 920 |
| Concrete + Tubes + Polysty Ribs | 0.016 | 1.47 | 1813 | 954 |
| Polystyrene 1 | 0.035 | 0.0853 a | 16 | 1200 |
| Plastic Lining | 0.002 | 0.124 | 265 | 1170 |
| Concrete Slab | 0.065 | 1.75 | 2200 | 950 |
| Insulated Block 1 | 0.070 | 0.0853 a | 18 | 1200 |
| Insulated Block 2 | 0.050 | 0.0853 a | 18 | 1200 |
| Polystyrene 2 | 0.030 | 0.0853 a | 18 | 1200 |
| Plasterboard | 0.013 | 0.35 | 850 | 800 |

a.  Imputed value for Case ET110B1.

Table 35b: Characteristics of the floor – Path 2 (Case ET110B1)

(Net inside surface area = 1.4700 m²)

| Material | d Thickness [m] | k Conductivity [W/mK] | Density [kg/m3] | Cp Specific heat [J/kgK] |
| --- | --- | --- | --- | --- |
| Ceramic Tile | 0.006 | 1.75 | 2177 | 920 |
| Glue Cement | 0.003 | 1.50 | 1900 | 840 |
| Concrete | 0.008 | 1.75 | 2177 | 920 |
| Concrete + Tubes + Polysty Ribs | 0.016 | 1.47 | 1813 | 954 |
| Polystyrene 1 | 0.035 | 0.0853 a | 16 | 1200 |
| Plastic Lining | 0.002 | 0.124 | 265 | 1170 |
| Concrete Slab | 0.065 | 1.75 | 2200 | 950 |
| Insulated Block 1 | 0.070 | 0.0853 a | 18 | 1200 |
| Concrete Beam 2 | 0.050 | 1.75 | 2200 | 950 |
| Polystyrene 2 | 0.030 | 0.0853 a | 18 | 1200 |
| Plasterboard | 0.013 | 0.35 | 850 | 800 |

a.  Imputed value for Case ET110B1.

Table 35c: Characteristics of the floor – Path 3 (Case ET110B1)

(Net inside surface area = 1.4700 m²)

| Material | d Thickness [m] | k Conductivity [W/mK] | Density [kg/m3] | Cp Specific heat [J/kgK] |
| --- | --- | --- | --- | --- |
| Ceramic Tile | 0.006 | 1.75 | 2177 | 920 |
| Glue Cement | 0.003 | 1.50 | 1900 | 840 |
| Concrete | 0.008 | 1.75 | 2177 | 920 |
| Concrete + Tubes + Polysty Ribs a | 0.016 | 1.47 | 1813 | 954 |
| Polystyrene 1 | 0.035 | 0.0853 a | 16 | 1200 |
| Plastic Lining | 0.002 | 0.124 | 265 | 1170 |
| Concrete Slab | 0.065 | 1.75 | 2200 | 950 |
| Concrete Beam 1 | 0.070 | 1.75 | 2200 | 950 |
| Concrete Beam 2 | 0.050 | 1.75 | 2200 | 950 |
| Polystyrene 2 | 0.030 | 0.0853 a | 18 | 1200 |
| Plasterboard | 0.013 | 0.35 | 850 | 800 |

a.  Imputed value for Case ET110B1.

Table 36: Characteristics of the door (Case ET110B1)

(Net inside surface area = 1.8281 m²)

| Material | d Thickness [m] | k Conductivity [W/m.K] | Density [kg/m3] | Cp Specific heat [J/kg.K] |
| --- | --- | --- | --- | --- |
| Blended Wood/Air/Cardboard + Plywood + Plexiglass | 0.036 | 0.1514 a | 307 | 1317 |
| Blended Air Gap | 0.038 | 0.254 | 1.2 | 1000 |
| Styrodur (see Figure 14) | 0.060 | 0.0518 a | 18 | 1200 |

a.  Imputed value for Case ET110B1.

Table 37a: Characteristics of insulated windows – Path 1 (Case ET110B1)

(Net inside surface area = 0.9905 m²)

| Material | d Thickness [m] | k Conductivity [W/m.K] | Density [kg/m3] | Cp Specific heat [J/kg.K] |
| --- | --- | --- | --- | --- |
| Blended Glass/Air Gap /Glass | 0.020 | 0.124 | 1081 | 900 |
| Air Gap | 0.009 | 0.1292 a | 1.2 | 1000 |
| Glasswool 1 | 0.200 | 0.0688 a | 11 | 800 |
| Polystyrene 1 | 0.070 | 0.0688 a | 16 | 1200 |

a.  Imputed value for Case ET110B1.

Table 37b: Characteristics of insulated windows – Path 2 (Case ET110B1)

(Net inside surface area = 0.1385 m²)

| Material | d Thickness [m] | k Conductivity [W/m.K] | Density [kg/m3] | Cp Specific heat [J/kg.K] |
| --- | --- | --- | --- | --- |
| PVC | 0.062 | 0.16 | 1380 | 1000 |
| Glasswool 2 | 0.188 | 0.0688 a | 11 | 800 |
| Polystyrene 1 | 0.070 | 0.0688 a | 16 | 1200 |

a.  Imputed value for Case ET110B1.

Table 37c: Characteristics of insulated windows – Path 3 (Case ET110B1)

(Net inside surface area = 0.6734 m²)

| Material | d Thickness [m] | k Conductivity [W/m.K] | Density [kg/m3] | Cp Specific heat [J/kg.K] |
| --- | --- | --- | --- | --- |
| Blended PVC + facing + plasterboard b | 0.062 | 3.5128 a | 1442 | 975 |
| Glasswool 3 c | 0.188 | 2.7444 a | 316 | 808 |
| Polystyrene 2 c | 0.070 | 2.7444 a | 320 | 1145 |

a.  Imputed value for Case ET110B1.

b. As a modeling simplification, the Path-3 window frame material includes the external setback cavity facing (known thermal bridge) and the plasterboard covering the facing on the test cell interior surface; see Appendix C for supporting information.

c. As a modeling simplification, the Glasswool 3 and Polystyrene 2 materials include the external setback cavity facing (known thermal bridge); see Appendix C for supporting information.

2.2.3.7	Surface Radiative Properties

The Cell B surface radiative properties shall be the same as for Cell A (see Section 2.2.1.7.3), except the east and west wall properties are exchanged as shown in Table 37tk.

Table 37tk Surface Radiative Properties of Cell A East and West Walls a

| Opaque Surface | Interior Radiative Properties |  | Exterior Radiative Properties |  |
| --- | --- | --- | --- | --- |
|  | Solar Absorptivity | Infrared Emissivity/ Absorptivity | Solar Absorptivity | Infrared Emissivity/ Absorptivity |
| East wall | 0.343 | 0.870 | 0.343 | 0.870 |
| West wall | 0.343 | 0.870 | 0.419 | 0.919 |

a. Properties are from Neymark et al. (2004), except where otherwise noted.

2.2.3.8	Surface Heat Transfer

The Cell B constant interior and exterior combined convective and radiative surface coefficients ((h,comb,int and h,comb,ext, respectively)) shall be the same as for Cell A (see Section 2.2.1.7.4), except the east and west wall coefficients are exchanged as shown in Table 38.

Table 38 Interior and Exterior Combined Surface Heat Transfer Coefficients of Cell B East and West Walls

|  | Interior Surface h,comb,int (W/(m2K)) | Exterior Surface h,comb,ext (W/(m2K)) |
| --- | --- | --- |
| East wall | 5.3 | 18 |
| West wall | 7.0 | 18 |
| Insulated Window West (like Cell A, East; see Table 17) |  |  |
| Path 1 (through glass) | 7.0 | 18 |
| Path 2 (through inner frame) | 7.0 | 18 |
| Path 3 (through blended outer frame) | 12.0 | 18 |

Informative Notes:

- Values of Table 38 are based on measured data; see Appendix C for details.

- The values of Table 38 (and Table 17 of Section 2.2.1.7.4 for all other walls) are applied to develop imputed thermal conductivities of various wall constructions of Section 2.2.3.6; see Appendix C for details.

- Informative Note: The greater coefficient of insulated window Path 3 shown in Table 38 is the same as that determined for the uninsulated window (see Section 2.2.5.9). This is for consistency with Path 3 having greater insulation conductivities to account for thermal bridging and 3-D conduction (see Table 15c, informative note b).

- For programs that allow direct input of constant convective surface coefficients but not direct input of constant combined (radiative and convective) surface coefficients, input may be entered as follows: enter the appropriate values for interior and/or exterior surfaces as convective coefficients, and set respective surface emittances to 0 (or as low as the program being tested allows).

- Constant surface coefficients presented here apply only to this test suite as they are specified for each test case and were determined only for the given test-case configurations; they should not be assumed to apply beyond this test suite.

2.2.3.9	Infiltration

Infiltration = 0 ACH.

Informative Note: This is the same as for Cell A, see Section 2.2.1.7.6.

2.2.3.10 Internal gains

For Case ET110B1, hourly-integrated measured fan energy is included with the test data (see Section 2.2.3.3).

- Apply fan heat as a sensible internal gain that is 100% convective.

Informative Notes:

- For the ET110B1 data acquisition period, hourly fan energy ranges from 0 to 216 Wh/h.

- There are no other internal gains in the test cell (no lighting, no occupants, etc.).

2.2.3.11 Thermal Guards

While guard zone temperature data is fully available, guard zone construction details are approximate. Two methods of modeling guard zones are indicated depending on what the program being tested allows:

- For programs that allow guard zones to be modeled as bounding surface exterior boundary conditions, see Section 2.2.3.11.1

- For programs that require detailed modeling of guard-zone geometry (i.e., that do not have an option to model zones adjacent to the test cell as external boundary conditions), see Section 2.2.3.11.2

Informative Note: Modeling guard zones as exterior surface boundary conditions, as in Section 2.2.3.11.1, is recommended because such a model reduces complexity and therefore reduces the potential for input errors.

2.2.3.11.1 Modeling guard zones as exterior surface boundary conditions

- Apply separate guard-zone air temperatures to each test cell bounding surface as specified in Section 2.2.3.3

- Apply exterior combined surface heat transfer coefficients to test cell bounding surfaces as specified in Section 2.2.3.8.

- Skip the remaining instructions and proceed to Section 2.2.3.12

2.2.3.11.2 Detailed modeling of guard zone geometry and construction details

2.2.3.11.2.1 Geometry

Apply overall test cell geometry of Figures 6 through 8; see Section 2.2.1.7.1.3 (Case ET110A1)

2.2.3.11.2.2 Constructions

Apply instructions of Section 2.2.1.7.9.2.2 (Case ET110A1); see instructions specific to Cell B.

2.2.3.11.2.3 Guard Zone Interior Surface Heat Transfer

Apply instructions of Section 2.2.1.7.9.2.3 (Case ET110A1); see instructions specific to Cell B.

2.2.3.11.2.4 Guard Zone Exterior Surface Heat Transfer

Apply instructions of Section 2.2.1.7.9.2.4 (Case ET110A1); see instructions specific to Cell B.

2.2.3.11.2.5 Guard Zones Temperature Control and Data

Apply separate guard-zone air temperatures to each guard zone as specified in Section 2.2.3.3.

Informative Note: See informative notes with Section 2.2.1.7.9.2.5 (Case ET110A1).

2.2.3.12 Mechanical System

The mechanical system for Cell B shall be exactly the same as for Cell A, except as specified in the following sections.

2.2.3.12.1  Fan Energy

Fan energy shall be modeled as an internal gain (see Section 2.2.3.10) and shall not be modeled explicitly as part of the mechanical system. If the program being tested requires an air-distribution fan, it shall be specified to consume no energy. Informative Note: This is the same instruction as Case ET110A1 except the Cell B fan energy hourly data is as in Section 2.2.3.10.

2.2.3.12.2 Thermostat Set Point.

Apply setpoint values for test-cell air temperatures and guard-zone air temperatures included in the data file specified in Section 2.2.3.3.

### Case ET110B2: Artificial Climate, Steady-State Overall Building Loss Coefficient with Insulated Windows, Cell B, Applying Specified Catalog Material Properties (No Imputed Properties)

#### Informative Note: Objective and Method of the Test Case

Case ET110B2 is specified as an extension case based on Case ET110B1.

The catalog-only data case – where imputed insulation conductivities of the base case are replaced with nominal catalog values – is provided to:

- Indicate the importance of developing imputed conductivities assuming one-dimensional (1-D) conduction (what most models do) based on measured data versus applying only material properties from catalog data in otherwise the same model

- Allow modelers to run sensitivity tests to examine causes of the load differences between applying imputed conductivities and only catalog values (i.e., filling the gap in differences). Such sensitivities may include evaluating the effects of two-dimensional (2-D) or three-dimensional (3-D) conduction, construction imperfections, thermal bridges, surface heat transfer, etc.

This case is repeated for Cell B to compare the modeled range of steady-state heating energy difference for all-catalog versus selected-imputed inputs between both Cell A and Cell B, i.e., to compare heating energy difference for ET110B2 – ET110B1 and ET110A2 – ET110A1. There will be differences between these sensitivities because, though designed as twins, the test cells have as-built differences resulting in differences among measured UA values, as documented in the test specification.

For an idealized heating system (that effectively outputs building load), apply results comparisons as listed with Objectives and Methods for Case ET110A1; see Section 2.2.1.1 Informative Notes, Item 3.

#### Extension Case Basis

Case ET110B2 shall be modeled exactly the same as Case ET110B1 except for changes detailed in the following sections.

#### Output Requirements.

Provide output applying tab ET110B2 of the template ET100series-output-GMT+1….xlsx,  which is included with the accompanying electronic media. Output requirements and format of Section 2.2.3.4 (Case ET110B1) shall apply.

#### Test Cell Bounding Surface Material Constructions.

Changes shall be made to selected material thermal conductivities specified in Section 2.2.3.6. Catalog values replacing imputed values from Case ET110B1 are the same as for Case ET110A2 (see Section 2.2.2.4), except the east and west walls are juxtaposed. Such catalog values are indicated via footnotes and bold yellow-highlighted text in the following tables:

- Characteristics of the North wall: Table 18 replaces Table 30

- Characteristics of the West wall: Table 19 (Cell A East wall) replaces Table 31

- Characteristics of the South wall: Table 20 replaces Table 32

- Characteristics of the East wall: Table 21 (Cell A West wall) replaces Table 33

- Characteristics of the ceiling – Path 1: Table 22a replaces Table 34a

- Characteristics of the ceiling – Path 2: Table 22b replaces Table 34b

- Characteristics of the floor – Path 1: Table 23a replaces Table 35a

- Characteristics of the floor – Path 2: Table 23b replaces Table 35b

- Characteristics of the floor – Path 3: Table 23c replaces Table 35c

- Characteristics of the door: Table 24 replaces Table 36

- Characteristics of insulated windows – Path 1: Table 25a replaces Table 37a

- Characteristics of insulated windows – Path 2: Table 25b replaces Table 37b

- Characteristics of insulated windows – Path 3: Table 25c replaces Table 37c

#### Infiltration

2.2.4.5.1  For Case ET110B2, infiltration shall be:

- 0.02045 ACH

2.2.4.5.2  The model shall assume test cell infiltration air exchange is distributed equally with each guard zone; i.e., 1/6 of the total infiltration rate selected from the range above is attributed to each guard zone.

2.2.4.5.3  Informative Notes

1. The given infiltration ACH is an average based on two tracer-gas measurements as follows:

- 0.0069 ACH was measured about 6 weeks before running the test case

- 0.034 ACH was measured about 6 months after running the test case and after test cell reconfigurations for other experiments not related to this empirical validation work. A rate of 0.037 ACH was obtained for this test cell during the last data acquisition period about 9 months after the 0.034 ACH measurement.

2. The range of infiltration ACH gives an equivalent range of UA attributable to infiltration (UAinf) of:

- UAinf = 0.10 to 0.48 W/K (0.29 W/K average)

3. For supporting information, see Appendix C, Table C-2.

### Case ET100A1: Artificial Climate, Steady-State Overall Building Loss Coefficient with Uninsulated Windows, Cell A, Applying Specified Catalog Material Properties Except for Selected Imputed Insulation Conductivities

#### Informative Note: Objective and Method of the Test Case

Case ET100A1 is specified as an extension case based on the Cell A artificial climate base case (Case ET110A1).

Case ET100A1 has the same construction as ET110A1 except both the south and east windows are uninsulated. This construction provides:

- Basis for measuring the UA of the window insulation as UAwinins = (UAET100 – UAET110) / 2, for each window of Cell A

- Base case for many of the artificial and natural climate test cases

- Basis for other test cell characterization configurations applied for determining various measured thermal properties that are not specified as cases for the test suite.

Similarly as Case ET110A1, guard-zone temperatures were set to approximately Tguards = 10˚C (the data is nearer to 10.5°C to match where the cellar, associated with the more massive floor, was controlled) and test cell temperature set to TcellA = 35 ˚C. See data files listed in Section 2.2.5.3 for guard zone and test cell hourly temperatures (set points). For an idealized heating system (that effectively outputs building load), apply results comparisons as listed with Objectives and Methods for Case ET110A1; see Section 2.2.1.1 Informative Notes, Item 3.

#### Extension Case Basis and Revision Summary

Case ET100A1 shall be modeled exactly the same as Case ET110A1 except for changes detailed in the following sections.

2.2.5.3 Test Cell Conditions and Guard-Zone Temperatures

##### 2.2.5.3.1	Test Cell Measured Data and Weather Input Data

Hourly data files and the test data sets durations for Case ET100A1 are listed in Table 2.2.5-1(39). These data files are included with the accompanying electronic media; also see Readme-ET100series-Files.docx there. The data files apply the same conventions as Case ET110A1 (see Section 2.2.1.3.1).

The ET100A-Measurements-GMT+1.csv hourly data format is the same for the Case ET110A data as provided in Table 3 (see Section 2.2.1.3.1).

Table 2.2.5-1(39) Primary Data File Directory (Case ET100A1)

| File Name | Data Type | Time Step | Data Duration (“MM/DD/YYYY hh”) [GMT+1] |
| --- | --- | --- | --- |
| ET100A-Measurements-GMT+1.csv d | Test Cell A | Hour | 09/08/2000 16 through 09/18/2000 14 |
| ET110MeteoGMT+1_within_Melun -071530_MY.2000.epw a,b,c,d | Local ETNA weather inserted within Melun, France AMY data | Hour | 01/01/2000 01 through 12/31/2000 24 |

a. Informative Note: This is the same weather data provided for Case ET110A1. Unlike for the ET110 cases recorded during an earlier data period, local ETNA weather data was not recorded for the solely artificial-climate data period during which Case ET100 occurred, so only nearby Melun data is provided for this case.

b. Informative Note: Epw format is described at: http://climate.onebuilding.org/papers/EnergyPlus_Weather_File_Format.pdf.

c. Informative Note: In the artificial climate cases, for programs that model guard zones as boundary conditions applied to each test cell wall rather than as literal zones, the weather data is essentially dummy data – i.e., not used in the model other than to satisfy the requirement of most BPS software to have a weather data set.

d. Informative Note: For further supporting information regarding these data files, see Readme-ET100series-Files.docx and also Neymark et al. (2004).

#### 2.2.5.4 Simulation Duration

Time period of simulation: 09/08/2000 16:00 through 09/18/2000 14:00 (GMT+1); time period convention is MM/DD/YYYY hh:mm.

This is the same time period as the ET100A-Measurements-GMT+1.csv input file; see Section 2.2.5.3.1.

2.2.5.5	Output Requirements.

2.2.5.5.1 Provide output applying tab ET100A1 of the template ET100series-output-GMT+1….xlsx, which is included with the accompanying electronic media.

2.2.5.5.2 Output requirements and format of Section 2.2.1.6 (Case ET110A1) shall apply, except:

- Output shall be provided for the simulation duration time period indicated in Section 2.2.5.4.

- Section 2.2.5.5.3 regarding comparison of output replaces Section 2.2.1.6.3.

2.2.5.5.3 Comparing Software Output to Measured Data and Empirical Values Derived from Measured data.

Results comparisons shall be applied only for the given best steady-state period of the data; see Section 2.2.5.5.3.1.

The following measured data are provided for results comparisons for all models:

- Heater energy (Qhtr): see Section 2.2.5.5.3.2

The following empirical values derived from measured data are provided for software applying the 16 alternative 1-D conduction paths specified for this test case:

- Total surface heat fluxes (q,x,tot) for each conduction path (x): see Section 2.2.5.5.3.3

Informative Note (for Simulation Trials): See “Informative Note (for Simulation Trials)” with Section 2.2.1.6.3 (Case ET110A1).

2.2.5.5.3.1 Application of Best Steady-State Data

For Case ET100A1, the best steady-state time period is:

9/16/2000 8:00 to 9/18/2000 14:00, GMT+1

(The time interval applies “MM/DD/YYYY hh:mm” format and preceding hour interval time convention of Section 2.1.1)

Informative Note: Determination of the best steady-state period for a given test case is described in Appendix C.

2.2.5.5.3.2 Comparison of Required Heater Energy (Qhtr) Results

The primary results comparison is for Qhtr provided in ET100A-Measurements-GMT+1.csv (see Section 2.2.5.3.1), corresponding with the best steady-state period (last 55 rows of the csv file).

Informative Note: If the program has input the test case correctly, for steady-state output it is reasonable to expect modeled hourly output Qhtr during the best steady-state period that is mostly within averaged measured Qhtr ± u(Q), Here, u(Q) is ± 0.7%[tk] for a 2-sigma (95% confidence interval) uncertainty band.

2.2.5.5.3.3 Comparison of Optional Inside Surface Flux Results

For software applying the 16 alternative 1-D conduction paths specified for this test case, total surface fluxes (q,x,tot) derived from measurements are provided in the file ET100series-MeasBasedSurfFlux-GMT+1.xlsx, see tab ‘ET100A’. Format of this file is provided in Table 5a (see Section 2.2.1.6.3.3 [Case ET110A1]).

For the purpose of this comparison, data is only provided for the best steady-state; see the last 55 rows of ET100series-MeasBasedSurfFlux-GMT+1.xlsx, tab ‘ET100A’.

Informative Notes:

- These fluxes are provided for the purpose of comparing best-steady-state-period modeled individual conduction-path inside surfaces fluxes to measurement-based individual conduction-path heat fluxes derived from empirical measurements.

- At steady state, modeled total inside surface fluxes and measurement-based individual conduction-path heat fluxes should be approximately equal.

- Derivation of hourly q,x,tot at best steady-state is provided in ET100series-MeasBasedSurfFlux-GMT+1.xlsx, tab ‘ET100A-SurfFluxDeriv’. Determination of measured UA values applied for this derivation is described in Appendix C.

2.2.5.6	Geometry.

2.2.5.6.1  Walls with windows (south and east)

Informative notes:

1. Removal of window insulation for case ET110A1 has no effect on the south and east window geometry specifications of Sections 2.2.1.7.1.2.2 and 2.2.7.1.2.4, respectively.

2. In artificial-climate cases the windows may be modeled as walls, or subsections of walls, because there is no transmitted solar radiation.

2.2.5.7	Test Cell Bounding Surface Material Constructions.

The following sections specify material constructions of the test cell bounding surfaces and subsurfaces:

- Required characteristics (Section 2.2.5.7.1)

- Alternative construction properties tables (Section 2.2.5.7.2)

###### 2.2.5.7.1 Required Characteristics

Table 2.2.5-2(40) specifies UA values for the south and east walls (including windows) and cross-references required geometry and construction figures for each wall. Informative Notes:

1. These overall wall UA-values (without window insulation) are unchanged from Case ET110A1; they are provided here for clarity

2. All other bounding surface overall UA-values are also the same as for Case ET110A1.

Table 2.2.5-2(40) Cell A Required Characteristics of South and East Walls (Case ET100A1)

| Wall | UA Value, W/K | Geometry Figure | Construction Figures (Section) |
| --- | --- | --- | --- |
| South | 8.07 | Figure 3 a (Section 2.2.1.7.1.2.2) | Figure 10 a (Section 2.2.1.7.2.3.1) |
| East | 9.36 | Figure 4 a (Section 2.2.1.7.1.2.4) | Figure 10 a (Section 2.2.1.7.2.3.1) |
| Windows | Included with walls | Figures 3 and 4 a | Figure 2.2.5-1a(19a) |

a. Informative Note: Same figures as for Case ET110A1.

For modelers requiring further guidance to specify inputs of material properties, apply the alternative construction specification of Section 2.2.5.7.2 (following). Informative Note: Use of the Section 2.2.5.7.2 alternative is recommended (see Section 2.1.10).

###### 2.2.5.7.2 Alternative Construction Specification

2.2.5.7.2.1  If the modeler does not require further guidance to develop inputs as specified in Section 2.2.5.7.1, skip the remaining instructions and proceed to Section 2.2.5.8.

2.2.5.7.2.2  Window insulation shall be removed such that the window is uninsulated as shown in Figure 2.2.5-1a(19a). The uninsulated window is divided into three parallel 1-D conduction path segments corresponding to the method for which thermal conductivities of the selected material layers were externally imputed. Informative Note: See Appendix C for details regarding external imputation of thermal conductivities.

Figure 2.2.5-1b(19b) illustrates the three parallel 1-d conduction heat flow paths (Path 1, Path 2, and Path 3) to be applied in the simulations.

The following tables apply for window modeling, where the same 1-D conduction path net inside surface areas are applied (see table captions) as in Case ET110A1:

- Characteristics of uninsulated windows – Path 1: Table 2.2.5-3a(41a) replaces Table 15a

- Characteristics of uninsulated windows – Path 2: Table 2.2.5-3b(41b) replaces Table 15b

- Characteristics of uninsulated windows – Path 3: Table 2.2.5-3c(41c) replaces Table 15c.

Informative Note: Figures 2.2.5-1a(19a), 2.2.5-1b(19b) and Tables 2.2.5-3a(41a) through 2.2.5-3c(41c) are also applied for Case ET100B1 as specified in Section 2.2.6.7.

Figure 2.2.5-1a(19a): Window Vertical Section (window and frame assembly), through the window and external setback cavity looking downward (or upward) – NOT TO SCALE

- Notes: Informative Note: This figure is a simplification of the actual construction to reduce the greater chance for input errors with the more complicated actual construction. See Appendix C for greater detail.

Figure 2.2.5-1b(19b): Window vertical section view (window and frame assembly) of the insulated window parallel heat-flow paths, looking downward (or upward) – NOT TO SCALE

Table 2.2.5-3a(41a): Characteristics of uninsulated windows – Path 1 (ET100A1)

(Net inside surface area = 0.9905 m²)

| Material | d Thickness [m] | k Conductivity [W/m.K] | Density [kg/m3] | Cp Specific heat [J/kg.K] |
| --- | --- | --- | --- | --- |
| Blended Glass/Air Gap /Glassa | 0.020 | 0.124 | 1081 | 900 |

a. Informative Note: See Appendix C for supporting information. This representation is consistent with the configuration applied for developing the imputed conductivities elsewhere. A more detailed window consistent with the blended values here, will be provided for the natural climate cases.

Table 2.2.5-3b(41b): Characteristics of uninsulated windows – Path 2 (ET100A1)

(Net inside surface area = 0.1385 m²)

| Material | d Thickness [m] | k Conductivity [W/m.K] | Density [kg/m3] | Cp Specific heat [J/kg.K] |
| --- | --- | --- | --- | --- |
| PVC | 0.062 | 0.16 | 1380 | 1000 |

Table 2.2.5-3c(41c): Characteristics of uninsulated windows – Path 3 (ET100A1)

(Net inside surface area = 0.6734 m²)

| Material | d Thickness [m] | k Conductivity [W/m.K] | Density [kg/m3] | Cp Specific heat [J/kg.K] |
| --- | --- | --- | --- | --- |
| Blended PVC + facing + plasterboard a | 0.062 | 0.267 b,c | 1442 | 975 |

a. Informative Note: As a modeling simplification, the Path-3 window frame material includes the external setback cavity facing (known thermal bridge) and the plasterboard covering the facing on the test cell interior surface; see Appendix C for supporting information.

b. Blended value based on catalog properties replacing imputed values from Case ET110A1.

c. Informative Note: For Case ET110A1 (and ET110B1), imputed window insulation conductivities were detemined separately from imputed opaque wall conductivities, where separate ET110A1 and ET110B1 opaque wall imputations (which are separately the same for ET100A1 and ET100B1, respectively) apply the uninsulated window catalog-based “Blended PVC + facing + plasterboard” properties shown here. Thus, application of this catalog-based value for Case ET100A1 (and ET100B1) is consistent with development of imputed values elsewhere. See Appendix C and “Imputation_of_k_insulation_ET110AB.xlsm” (included with accompanying electronic media) for supporting information.

2.2.5.8	Surface Radiative Properties

The uninsulated window glazing and frame surface radiative properties are as shown in Table 2.2.5-4(42).

Table 2.2.5-4(42) Surface Radiative Properties of Uninsulated Windows (ET100A1) a

| Window Surface | Interior Radiative Properties |  | Exterior Radiative Properties |  |
| --- | --- | --- | --- | --- |
|  | Solar Absorptivity | Infrared Emissivity/ Absorptivity | Solar Absorptivity | Infrared Emissivity/ Absorptivity |
| Glass | 0.129 | 0.9 | 0.129 | 0.9 |
| Frame | 0.343 | 0.870 | 0.343 | 0.870 |

a. Properties varying from Case ET110A1 (and Case ET110B1) are highlighted in bold font.

Informative Note: Table 2.2.5-4(42) is also applied for Case ET100B1 as specified in Section 2.2.6.8.

2.2.5.9	Interior Surface Heat Transfer

The coefficients (h,comb,int) of Table 2.2.5-5(43) shall be applied to the given window glazing and frame conduction paths. Informative Note: The exterior surface coefficients remain the same as in Case ET110A1.

Table 2.2.5-5(43)  Interior Combined Surface Heat Transfer Coefficients of Cell A Window (ET100A1) a

|  | Interior Surface h,comb,int (W/(m2K)) |
| --- | --- |
| Path 1 (through glass) | 12.0 |
| Path 2 (through inner frame) | 12.0 |
| Path 3 (through blended outer frame) | 12.0 |

a. Properties varying from Case ET110A1 (and Case ET110B1) are highlighted in bold font.

Informative Notes:

- Table 2.2.5-5(43) is also applied for Case ET100B1 as specified in Section 2.2.6.9

- Values of Table 2.2.5-5(43) are based on measured data for uninsulated windows; see Appendix C for details. (The value for Path 3 here was also applied for Case ET110A1 per Informative Note 3 with Table 17.)

- For programs that allow direct input of constant convective surface coefficients but not direct input of constant combined (radiative and convective) surface coefficients, input may be entered as follows: enter the appropriate values for interior and/or exterior surfaces as convective coefficients, and set respective surface emittances to 0 (or as low as the program being tested allows).

- Constant surface coefficients presented here apply only to this test suite as they are specified for each test case and were determined only for the given test-case configurations; they should not be assumed to apply beyond this test suite.

2.2.5.10 Internal gains

For Case ET100A1, hourly-integrated measured fan energy is included with the test data (see Section 2.2.5.3).

Informative Note: For the ET100A1 data acquisition period, hourly fan energy ranges from 144.0 to 157.6 Wh/h.

2.2.5.11 Thermal Guards

While guard zone temperature data is fully available, guard zone construction details are approximate. Two methods of modeling guard zones are indicated depending on what the program being tested allows:

- For programs that allow guard zones to be modeled as bounding surface exterior boundary conditions, see Section 2.2.5.11.1

- For programs that require detailed modeling of guard-zone geometry (i.e., that do not have an option to model zones adjacent to the test cell as external boundary conditions), see Section 2.2.5.11.2

2.2.5.11.1 Modeling guard zones as exterior surface boundary conditions

- Apply separate guard-zone air temperatures to each test cell bounding surface as specified in Section 2.2.5.3

- Skip the remaining instructions and proceed to Section 2.2.5.12

2.2.5.11.2 Detailed modeling of guard zone geometry and construction details

- Apply separate guard-zone air temperatures to each guard zone as specified in Section 2.2.5.3

2.2.5.12 Mechanical System

2.2.3.12.1  Fan Energy

Fan energy shall be modeled as an internal gain as specified in Section 2.2.5.10.

2.2.3.12.2 Thermostat Set Point.

Apply setpoint values for test-cell air temperatures and guard-zone air temperatures included in the data file specified in Section 2.2.5.3.

### Case ET100B1: Artificial Climate, Steady-State Overall Building Loss Coefficient with Uninsulated Windows, Cell B, Applying Specified Catalog Material Properties Except for Selected Imputed Insulation Conductivities

#### Informative Note: Objective and Method of the Test Case

Case ET100B1 is specified as an extension case based on the Cell B artificial climate base case (Case ET110B1).

Case ET100B1 has the same construction as ET110B1 except both the south and west windows are uninsulated similarly to the south and east windows of Case ET100A1 (Section 2.2.5). This construction provides:

- Basis for measuring the UA of the window insulation as UAwinins = (UAET100 – UAET110) / 2, for each window of Cell B

- Base case for many of the artificial and natural climate test cases

- Basis for other test cell characterization configurations applied for determining various measured thermal properties that are not specified as cases for the test suite.

Similarly as Case ET110B1, guard-zone temperatures were set to approximately Tguards = 10˚C (the data is nearer to 10.5°C to match where the cellar, associated with the more massive floor, was controlled) and test cell temperature set to TcellB = 35 ˚C. See data files listed in Section 2.2.6.3 for guard zone and test cell hourly temperatures (set points). For an idealized heating system (that effectively outputs building load), apply results comparisons as listed with Objectives and Methods for Case ET110A1; see Section 2.2.1.1 Informative Notes, Item 3.

#### Extension Case Basis and Revision Summary

Case ET100B1 shall be modeled exactly the same as Case ET110B1 except for changes detailed in the following sections.

2.2.6.3 Test Cell Conditions and Guard-Zone Temperatures

##### 2.2.6.3.1	Test Cell Measured Data and Weather Input Data

Hourly data files and the test data sets durations for Case ET100B1 are listed in Table 2.2.6-1(44). These data files are included with the accompanying electronic media; also see Readme-ET100series-Files.docx there. The data files apply the same conventions as Case ET110A1 (see Section 2.2.1.3.1).

The ET100B-Measurements-GMT+1.csv hourly data format is the same for the Case ET110A data as provided in Table 3 (see Section 2.2.1.3.1).

Table 2.2.6-1(44) Primary Data File Directory (Case ET100B1)

| File Name | Data Type | Time Step | Data Duration (“MM/DD/YYYY hh”) [GMT+1] |
| --- | --- | --- | --- |
| ET100B-Measurements-GMT+1.csv d | Test Cell B | Hour | 09/08/2000 16 through 09/18/2000 15 |
| ET110MeteoGMT+1_within_Melun -071530_MY.2000.epw a,b,c,d | Local ETNA weather inserted within Melun, France AMY data | Hour | 01/01/2000 01 through 12/31/2000 24 |

a. Informative Note: This is the same weather data provided for Case ET100A1; see Informative Note “a” with Table 2.2.5-1(39).

b. Informative Note: Epw format is described at: http://climate.onebuilding.org/papers/EnergyPlus_Weather_File_Format.pdf.

c. Informative Note: In the artificial climate cases, for programs that model guard zones as boundary conditions applied to each test cell wall rather than as literal zones, the weather data is essentially dummy data – i.e., not used in the model other than to satisfy the requirement of most BPS software to have a weather data set.

d. Informative Note: For further supporting information regarding these data files, see Readme-ET100series-Files.docx and also Neymark et al. (2004).

#### 2.2.6.4 Simulation Duration

Time period of simulation: 09/08/2000 16:00 through 09/18/2000 15:00 (GMT+1); time period convention is MM/DD/YYYY hh:mm.

This is the same time period as the ET100B-Measurements-GMT+1.csv input file; see Section 2.2.6.3.1.

2.2.6.5	Output Requirements.

2.2.6.5.1 Provide output applying tab ET100B1 of the template ET100series-output-GMT+1….xlsx,  which is included with the accompanying electronic media.

2.2.6.5.2 Output requirements and format of Section 2.2.3.4 (Case ET110B1) shall apply, except:

- Output shall be provided for the simulation duration time period indicated in Section 2.2.6.4

- Section 2.2.6.5.3 regarding comparison of output replaces Section 2.2.3.4.3.

2.2.6.5.3 Comparing Software Output to Measured Data and Empirical Values Derived from Measured data.

Results comparisons shall be applied only for the given best steady-state period of the data; see Section 2.2.6.5.3.1.

The following measured data are provided for results comparisons for all models:

- Heater energy (Qhtr): see Section 2.2.6.5.3.2

The following empirical values derived from measured data are provided for software applying the 16 alternative 1-D conduction paths specified for this test case:

- Total surface heat fluxes (q,x,tot) for each conduction path (x): see Section 2.2.6.5.3.3

Informative Note (for Simulation Trials): See “Informative Note (for Simulation Trials)” with Section 2.2.1.6.3 (Case ET110A1).

2.2.6.5.3.1 Application of Best Steady-State Data

For Case ET100B1, the best steady-state time period is:

9/16/2000 8:00 to 9/18/2000 14:00, GMT+1

(The time interval applies “MM/DD/YYYY hh:mm” format and preceding hour interval time convention of Section 2.1.1)

Informative Notes:

1. This is the same best steady-state time period as in Case ET100A1

2. Determination of the best steady-state period for a given test case is described in Appendix C.

2.2.6.5.3.2 Comparison of Required Heater Energy (Qhtr) Results

The primary results comparison is for Qhtr provided in ET100B-Measurements-GMT+1.csv (see Section 2.2.6.3.1), corresponding with the best steady-state period (last 55 rows of the csv file).

Informative Note: If the program has input the test case correctly, for steady-state output it is reasonable to expect modeled hourly output Qhtr during the best steady-state period that is mostly within averaged measured Qhtr ± u(Q), Here, u(Q) is ± 0.9%[tk] for a 2-sigma (95% confidence interval) uncertainty band.

2.2.6.5.3.3 Comparison of Optional Inside Surface Flux Results

For software applying the 16 alternative 1-D conduction paths specified for this test case, total surface fluxes (q,x,tot) derived from measurements are provided in the file ET100series-MeasBasedSurfFlux-GMT+1.xlsx, see tab ‘ET100B’. Format of this file is provided in Table 2.2.3-3a(28a) (see Section 2.2.3.4.3.3 [Case ET110B1]).

For the purpose of this comparison, data is only provided for the best steady-state; see the last 55 rows of ET100series-MeasBasedSurfFlux-GMT+1.xlsx, tab ‘ET100B’.

Informative Notes:

- These fluxes are provided for the purpose of comparing best-steady-state-period modeled individual conduction-path inside surfaces fluxes to measurement-based individual conduction-path heat fluxes derived from empirical measurements.

- At steady state, modeled total inside surface fluxes and measurement-based individual conduction-path heat fluxes should be approximately equal.

- Derivation of hourly q,x,tot at best steady-state is provided in ET100series-MeasBasedSurfFlux-GMT+1.xlsx, tab ‘ET100B-SurfFluxDeriv’. Determination of measured UA values applied for this derivation is described in Appendix C.

2.2.6.6	Geometry.

2.2.6.6.1  Walls with windows (south and west)

Informative notes:

1. Removal of window insulation for case ET110B1 has no effect on the south and west window geometry specifications of Sections 2.2.1.7.1.2.2 (same as Cell A) and 2.2.3.5.2.2 (Cell B), respectively.

2. In artificial-climate cases the windows may be modeled as walls, or subsections of walls, because there is no transmitted solar radiation.

2.2.6.7	Test Cell Bounding Surface Material Constructions.

The following sections specify material constructions of the test cell bounding surfaces and subsurfaces:

- Required characteristics (Section 2.2.6.7.1)

- Alternative construction properties tables (Section 2.2.6.7.2)

###### 2.2.6.7.1 Required Characteristics

Table 2.2.6-2(45) specifies UA values for the south and west walls (including windows) and cross-references required geometry and construction figures for each wall. Informative Notes:

1. These overall wall UA-values (without window insulation) are unchanged from Case ET110B1; they are provided here for clarity

2. All other bounding surface overall UA-values are also the same as for Case ET110B1.

Table 2.2.6-2(45) Cell B Required Characteristics of South and East Walls (Case ET100B1)

| Wall | UA Value, W/K | Geometry Figure | Construction Figures (Section) |
| --- | --- | --- | --- |
| South | 8.68 | Figure 3 a (Section 2.2.1.7.1.2.2) | Figure 10 a (Section 2.2.1.7.2.3.1) |
| West | 8.94 | Figure 18 b (Section 2.2.1.7.1.2.4) | Figure 10 a (Section 2.2.1.7.2.3.1) |
| Windows | Included with walls | Figures 3 a and 18 b | Figure 2.2.5-1a(19a) c (Section 2.2.5.7) |

a. Informative Note: Same figures as for Case ET110A1 and ET110B1.

b. Informative Note: Same figure as for Case ET110B1.

c. Informative Note: Same figure as for Case ET100A1.

For modelers requiring further guidance to specify inputs of material properties, apply the alternative construction specification of Section 2.2.6.7.2 (following). Informative Note: Use of the Section 2.2.6.7.2 alternative is recommended (see Section 2.1.10).

###### 2.2.6.7.2 Alternative Construction Specification

2.2.6.7.2.1  If the modeler does not require further guidance to develop inputs as specified in Section 2.2.6.7.1, skip the remaining instructions and proceed to Section 2.2.6.8.

2.2.6.7.2.2  Window insulation shall be removed such that the window is uninsulated as shown in Figure 2.2.5-1a(19a) (Case ET100A1). As with Case ET100A1, the uninsulated window is divided into three parallel 1-D conduction path segments corresponding to the method for which thermal conductivities of the selected material layers were externally imputed. Informative Note: See Appendix C for details regarding external imputation of thermal conductivities.

Figure 2.2.5-1b(19b) (Case ET100A1) illustrates the three parallel 1-d conduction heat flow paths (Path 1, Path 2, and Path 3) to be applied in the simulations.

The following tables from Case ET100A1 apply for window modeling for Case ET100B1, where the same 1-D conduction path net inside surface areas are applied (see table captions) as in Cases ET110A1 and ET110B1:

- Characteristics of uninsulated windows – Path 1: Table 2.2.5-3a(41a) (Case ET100A1) replaces Table 37a (Case ET110B1)

- Characteristics of uninsulated windows – Path 2: Table 2.2.5-3b(41b) (Case ET100A1) replaces Table 37b (Case ET110B1)

- Characteristics of uninsulated windows – Path 3: Table 2.2.5-3c(41c) (Case ET100A1) replaces Table 37c (Case ET110B1).

2.2.6.8	Surface Radiative Properties

The uninsulated window glazing and frame surface radiative properties are as shown in Table 2.2.5-4(42) (Case ET100A1).

2.2.6.9	Interior Surface Heat Transfer

The coefficients (h,comb,int) of Table 2.2.5-5(43) (Case ET100A1) shall be applied to the given window glazing and frame conduction paths.

2.2.6.10 Internal gains

For Case ET100B1, hourly-integrated measured fan energy is included with the test data (see Section 2.2.6.3).

Informative Note: For the ET100B1 data acquisition period, hourly fan energy ranges from 148.0 to 168.0 Wh/h.

2.2.6.11 Thermal Guards

While guard zone temperature data is fully available, guard zone construction details are approximate. Two methods of modeling guard zones are indicated depending on what the program being tested allows:

- For programs that allow guard zones to be modeled as bounding surface exterior boundary conditions, see Section 2.2.6.11.1

- For programs that require detailed modeling of guard-zone geometry (i.e., that do not have an option to model zones adjacent to the test cell as external boundary conditions), see Section 2.2.6.11.2.

2.2.6.11.1 Modeling guard zones as exterior surface boundary conditions

- Apply separate guard-zone air temperatures to each test cell bounding surface as specified in Section 2.2.6.3

- Skip the remaining instructions and proceed to Section 2.2.6.12

2.2.6.11.2 Detailed modeling of guard zone geometry and construction details

- Apply separate guard-zone air temperatures to each guard zone as specified in Section 2.2.6.3

2.2.6.12 Mechanical System

2.2.6.12.1  Fan Energy

Fan energy shall be modeled as an internal gain as specified in Section 2.2.6.10

2.2.6.12.2 Thermostat Set Point.

Apply setpoint values for test-cell air temperatures and guard-zone air temperatures included in the data file specified in Section 2.2.6.3.

    - 2.2.7 	Case ET100A3: Artificial Climate, Steady-State Overall Building Loss Coefficient with Uninsulated Windows, Cell A, Applying Specified Catalog Material Properties Except for Selected Imputed Insulation Conductivities – with User Selected Interior Surface Heat Transfer Algorithms

      - 2.2.7.1 Informative Notes: Objective and Method of the Test Case

1. Case ET100A3 is the same as ET100A1 except the constant combined surface heat transfer coefficients are replaced with surface heat transfer algorithms selected by the modeler. This provides an empirical validation of surface heat transfer algorithms for use with the ETNA test cases based on comparisons of modeled results versus measured data ± measurement uncertainty (μ).

2. For an idealized heating system (that effectively outputs building load), apply comparisons during the best steady-state period of the empirical data for the following results:

- As listed with Objectives and Methods for Case ET110A1; see Section 2.2.1.1 Informative Notes, Item 3.

  - With respect to Qsurf,n,model vs Qwall,n,measured, for this test case it may be reasonable to expect greater differences for modeled versus measured data for bounding surfaces with greater UA values, because surface heat transfer may represent a greater proportion of overall thermal resistance for such surfaces.

- hcomb,int,n,model vs hcomb,int,n,measured, where

  - hcomb,int,n,model = Qsurf,n,model / (Tcell,model – Tsurf,int,n,model), where

    - Tcell,model ≡ model test cell temperature output (should be same as measured Tcell)

    - Tsurf,int,n,model ≡ model interior surface temperature output

  - hcomb,int,n,measured is the measured combined coefficient based on characterization test case measurements, as documented in Appendix C

  - Propagated μ(hcomb,int,n,measured) provided by the test spec developers

      - 2.2.7.2 Extension Case Basis and Revision Summary

Case ET100A3 shall be modeled exactly the same as Case ET100A1 except for changes detailed in the following sections.

2.2.7.3	Output Requirements.

2.2.7.3.1 Provide output applying tab ET100A3 of the template ET100series-output-GMT+1….xlsx, which is included with the accompanying electronic media.

2.2.7.3.2 Output requirements and format of Section 2.2.5.5 (Case ET100A1) shall apply, except:

- For software applying the 16 alternative 1-D conduction paths specified for this test case, inside surface temperature output shall also be provided as specified in Section 2.2.7.3.3

- Section 2.2.7.3.4 regarding comparison of output replaces Section 2.2.5.5.3.

2.2.7.3.3 Inside surface temperature output

For software applying the 16 alternative 1-D conduction paths specified for this test case, the following output shall be provided:

- Hourly integrated-average inside surface temperatures (°C) output as specified in Table 2.2.7-1(46); these are the temperatures of each surface at its interior face

- This output shall be provided as allowed by the software being tested.

- This output corresponds with each 1-D conduction path specified for the test case.

Table 2.2.7-1(46).  Appended Hourly Inside Surface Temperature Output (ET100A3) a

| Column | Label | Description | Units |
| --- | --- | --- | --- |
| BH | T,c1 | Ceiling Path 1 inside surface temperature | °C |
| BI | T,c2 | Ceiling Path 2 inside surface temperature | °C |
| BJ | T,f1 | Floor Path 1 inside surface temperature | °C |
| BK | T,f2 | Floor Path 2 inside surface temperature | °C |
| BL | T,f3 | Floor Path 3 inside surface temperature | °C |
| BM | T,n | North wall inside surface temperature | °C |
| BN | T,d | Door inside surface temperature | °C |
| BO | T,e | East wall inside surface temperature | °C |
| BP | T,ewin1 | East window Path 1 inside surface temperature | °C |
| BQ | T,ewin2 | East window Path 2 inside surface temperature | °C |
| BR | T,ewin3 | East window Path 3 inside surface temperature | °C |
| BS | T,s | South wall inside surface temperature | °C |
| BT | T,swin1 | South window Path 1 inside surface temperature | °C |
| BU | T,swin2 | South window Path 2 inside surface temperature | °C |
| BV | T,swin3 | South window Path 3 inside surface temperature | °C |
| BW | T,w | West wall inside surface temperature | °C |

a. See Section 2.2.7.3.1.

2.2.7.3.4 Comparing Software Output to Measured Data and Empirical Values Derived from Measured data.

Results comparisons shall be applied only for the given best steady-state period of the data; see Section 2.2.7.3.4.1.

The following measured data are provided for results comparisons for all models:

- Heater energy (Qhtr): see Section 2.2.7.3.4.2

The following empirical values derived from measured data are provided for software applying the 16 alternative 1-D conduction paths specified for this test case:

- Total surface heat fluxes (q,x,tot) for each conduction path (n): see Section 2.2.7.3.4.3

Informative Note (for Simulation Trials): See “Informative Note (for Simulation Trials)” with Section 2.2.1.6.3 (Case ET110A1).

2.2.7.3.4.1 Application of Best Steady-State Data

For Case ET100A3, the best steady-state time period is (same as Case ET100A1):

9/16/2000 8:00 to 9/18/2000 14:00, GMT+1

(The time interval applies “MM/DD/YYYY hh:mm” format and preceding hour interval time convention of Section 2.1.1)

Informative Note: Determination of the best steady-state period for a given test case is described in Appendix C.

2.2.7.3.4.2 Comparison of Required Heater Energy (Qhtr) Results

The primary results comparison is for Qhtr provided in ET100A-Measurements-GMT+1.csv (see Section 2.2.5.3.1), corresponding with the best steady-state period (last 55 rows of the csv file).

Informative Note: An uncertainty band around Qhtr maybe be characterized by averaged measured Qhtr ± u(Q), Here, u(Q) is ± 0.7%[tk] for a 2-sigma (95% confidence interval) uncertainty band.

2.2.7.3.4.3 Comparison of Optional Surface Flux Results

For software applying the 16 alternative 1-D conduction paths specified for this test case, total surface fluxes (q,x,tot) derived from measurements are provided in the file ET100series-MeasBasedSurfFlux-GMT+1.xlsx, see tab ‘ET100A’ (same measurement-based data applies for Cases ET100A3 and ET100A1). Format of this file is provided in Table 5a (see Section 2.2.1.6.3.3 [Case ET110A1]).

For the purpose of this comparison, data is only provided for the best steady-state; see the last 55 rows of ET100series-MeasBasedSurfFlux-GMT+1.xlsx, tab ‘ET100A’.

Informative Notes:

- These fluxes are provided for the purpose of comparing best-steady-state-period modeled individual conduction-path surfaces fluxes to measurement-based individual conduction-path heat fluxes derived from empirical measurements.

- For Case ET100A3, best-steady-state modeled total surface fluxes may vary from measurement-based individual conduction-path heat fluxes.

- Derivation of hourly q,x,tot at best steady-state is provided in ET100series-MeasBasedSurfFlux-GMT+1.xlsx, tab ‘ET100A-SurfFluxDeriv’. Determination of measured UA values applied for this derivation is described in Appendix C.

2.2.7.3.4.4 Comparison of Interior Surface Temperature (T,intsurf,x) Results

The following applies for software applying the 16 alternative 1-D conduction paths specified for this test case.

Informative Notes (for Simulation Trials):

- For comparing T,intsurf,x results, the ETNA project team will develop equivalent modeled interior combined convective and radiative surface coefficients (h,comb,int,x) for each conduction path based on modeled h,comb,int,x = q,x,tot / (Tcell – T,intsurf,x)

- The effective modeled combined coefficients will be compared to the measured interior combined coefficients given for Case ET100A1, as specified in Sections 2.2.1.7.4 (Case ET110A1) and 2.2.5.9 (ET100A1).

- In this comparison, h,comb,int,x as proxy for T,intsurf,x provides a better basis for scaling modeled versus measurement-based temperature differences than directly comparing modeled T,intsurf,x with T,intsurf,x derived from measurements.

2.2.7.4	Interior Surface Heat Transfer

2.2.7.4.1 Interior Surface Heat Transfer Model.

The modeler shall select the following as allowed by their program:

- A time-step varying interior surface convection heat transfer algorithm, or constant surface convection coefficient(s) applied to each conduction path interior surface face

  - For tested programs with multiple options for time-step varying interior surface convection algorithms, the user shall select the most appropriate algorithm based on the test cell geometry and construction and the heating system fan supply airflow rate provided in the accompanying file ET100A-GMT+1.csv (see Section 2.2.5.3.1 [Case ET100A1])

- A time-step varying interior surface infrared radiation exchange algorithm.

  - For tested programs with multiple options for time-step varying radiation exchange algorithms, the user shall select the most appropriate algorithm based on the test cell geometry and construction.

The modeler shall indicate the applied algorithms or values in Item S2 of their pro-forma modeler report; see ModRep_Proforma_ET100series(mmddyy).docx included with the accompanying electronic media.

Informative notes:

- This replaces the constant interior combined convective and radiative surface heat transfer coefficients specified for Case ET100A1

- Fan supply airflow rate varies hourly around an average of approximately 20.7 ACH for the best steady-state data period of this test case

- During pre-trial sensitivity tests, the spec authors observed a substantial difference between model results for buoyancy-driven versus mechanically driven interior surface heat transfer algorithms

- Constant convection-only coefficients are not provided in this test specification

- The exterior surface coefficients remain the same as in Case ET100A1.

2.2.7.4.2 Interior Surface Texture.

For programs that allow variation of interior surface convection with surface texture, interior surface texture shall be selected within the tested program to best match the surface material indicated in Table 2.2.7-2(47)

Table 2.2.7-2(47) Interior Surface Type, Case ET100A3

| Surface Type | Surface Material |
| --- | --- |
| Walls | Wallpaper |
| Ceiling | Wallpaper |
| Floor | Ceramic tile |
| Door | Wood, painted |
| Window panes | Glass |
| Window frames | PVC |

    - 2.2.8 	Case ET100B3: Artificial Climate, Steady-State Overall Building Loss Coefficient with Uninsulated Windows, Cell B, Applying Specified Catalog Material Properties Except for Selected Imputed Insulation Conductivities – with User Selected Interior Surface Heat Transfer Algorithms

      - 2.2.8.1 Informative Note: Objective and Method of the Test Case

Case ET100B3 is the same as ET100B1 except the constant combined surface heat transfer coefficients are replaced with surface heat transfer algorithms selected by the modeler. This provides an empirical validation of surface heat transfer algorithms for use with the ETNA test cases based on comparisons of modeled results versus measured data ± measurement uncertainty (μ).

For an idealized heating system (that effectively outputs building load), apply comparisons as listed with Objectives and Methods for Case ET100A3; see Section 2.2.7.1 Informative Notes, Item 2.

      - 2.2.8.2 Extension Case Basis and Revision Summary

Case ET100B3 shall be modeled exactly the same as Case ET100B1 except for changes detailed in the following sections.

2.2.8.3	Output Requirements.

2.2.8.3.1 Provide output applying tab ET100B3 of the template ET100series-output-GMT+1….xlsx, which is included with the accompanying electronic media.

2.2.8.3.2 Output requirements and format of Section 2.2.6.5 (Case ET100B1) shall apply, except:

- For software applying the 16 alternative 1-D conduction paths specified for this test case, inside surface temperature output shall also be provided as specified in Section 2.2.8.3.3.

- Section 2.2.8.3.4 regarding comparison of output replaces Section 2.2.6.5.3.

2.2.8.3.3 Inside surface temperature output

For software applying the 16 alternative 1-D conduction paths specified for this test case, the following output shall be provided:

- Hourly integrated-average inside surface temperatures (°C) output as specified in Table 2.2.8-1(48); these are the temperatures of each surface at its interior face

- This output shall be provided as allowed by the software being tested.

- This output corresponds with each 1-D conduction path specified for the test case.

Table 2.2.8-1(48).  Appended Hourly Inside Surface Temperature Output (ET100B3) a

| Column | Label | Description | Units |
| --- | --- | --- | --- |
| BH | T,c1 | Ceiling Path 1 inside surface temperature | °C |
| BI | T,c2 | Ceiling Path 2 inside surface temperature | °C |
| BJ | T,f1 | Floor Path 1 inside surface temperature | °C |
| BK | T,f2 | Floor Path 2 inside surface temperature | °C |
| BL | T,f3 | Floor Path 3 inside surface temperature | °C |
| BM | T,n | North wall inside surface temperature | °C |
| BN | T,d | Door inside surface temperature | °C |
| BO | T,e | East wall inside surface temperature | °C |
| BP | T,s | South wall inside surface temperature | °C |
| BQ | T,swin1 | South window Path 1 inside surface temperature | °C |
| BR | T,swin2 | South window Path 2 inside surface temperature | °C |
| BS | T,swin3 | South window Path 3 inside surface temperature | °C |
| BT | T,w | West wall inside surface temperature | °C |
| BU | T,wwin1 | West window Path 1 inside surface temperature | °C |
| BV | T,wwin2 | West window Path 2 inside surface temperature | °C |
| BW | T,wwin3 | West window Path 3 inside surface temperature | °C |

a. See Section 2.2.8.3.1.

2.2.8.3.4 Comparing Software Output to Measured Data and Empirical Values Derived from Measured data.

Results comparisons shall be applied only for the given best steady-state period of the data; see Section 2.2.8.3.4.1.

The following measured data are provided for results comparisons for all models:

- Heater energy (Qhtr): see Section 2.2.8.3.4.2

The following empirical values derived from measured data are provided for software applying the 16 alternative 1-D conduction paths specified for this test case:

- Total surface heat fluxes (q,x,tot) for each conduction path (x): see Section 2.2.7.3.4.3

Informative Note: This is the same comparison method as in Case ET100A3, except references to sections, tables, and accompanying files are specific to this test case.

2.2.8.3.4.1 Application of Best Steady-State Data

For Case ET100B3, the best steady-state time period is (same as Case ET100B1):

9/16/2000 8:00 to 9/18/2000 14:00, GMT+1

(The time interval applies “MM/DD/YYYY hh:mm” format and preceding hour interval time convention of Section 2.1.1)

Informative Note: Determination of the best steady-state period for a given test case is described in Appendix C.

2.2.8.3.4.2 Comparison of Required Heater Energy (Qhtr) Results

The primary results comparison is for Qhtr provided in ET100B-Measurements-GMT+1.csv (see Section 2.2.6.3.1), corresponding with the best steady-state period (last 55 rows of the csv file).

Informative Note: An uncertainty band around Qhtr maybe be characterized by averaged measured Qhtr ± u(Q), Here, u(Q) is ± 0.9%[tk] for a 2-sigma (95% confidence interval) uncertainty band.

2.2.7.3.4.3 Comparison of Optional Surface Flux Results

For software applying the 16 alternative 1-D conduction paths specified for this test case, total surface fluxes (q,x,tot) derived from measurements are provided in the file ET100series-MeasBasedSurfFlux-GMT+1.xlsx, see tab ‘ET100B’ (same measurement-based data applies for Cases ET100B3 and ET100B1). Format of this file is provided in Table 2.2.3-3a(28a) (see Section 2.2.3.4.3.3 [Case ET110B1]).

For the purpose of this comparison, data is only provided for the best steady-state; see the last 55 rows of ET100series-MeasBasedSurfFlux-GMT+1.xlsx, tab ‘ET100B’.

Informative Notes:

- These fluxes are provided for the purpose of comparing best-steady-state-period modeled individual conduction-path surfaces fluxes to measurement-based individual conduction-path heat fluxes derived from empirical measurements.

- For Case ET100B3, best-steady-state modeled total surface fluxes may vary from measurement-based individual conduction-path heat fluxes.

- Derivation of hourly q,x,tot at best steady-state is provided in ET100series-MeasBasedSurfFlux-GMT+1.xlsx, tab ‘ET100B-SurfFluxDeriv’. Determination of measured UA values applied for this derivation is described in Appendix C.

2.2.8.3.4.4 Comparison of Interior Surface Temperature (T,intsurf,x) Results

The following applies for software applying the 16 alternative 1-D conduction paths specified for this test case.

Informative Notes (for Simulation Trials):

- For comparing T,intsurf,x results, the ETNA project team will develop equivalent modeled interior combined convective and radiative surface coefficients (h,comb,int,x) for each conduction path based on modeled h,comb,int,x = q,x,tot / (Tcell – T,intsurf,x)

- The effective modeled combined coefficients will be compared to the measured interior combined coefficients given for Case ET100B1, as specified in Sections 2.2.1.7.4 (Case ET110A1), 2.2.3.8 (ET110B1), and 2.2.6.8 (ET100B1).

- In this comparison, h,comb,int,x as proxy for T,intsurf,x provides a better basis for scaling modeled versus measurement-based temperature differences than directly comparing modeled T,intsurf,x with T,intsurf,x derived from measurements.

2.2.8.4	Interior Surface Heat Transfer

2.2.8.4.1 Interior Surface Heat Transfer Model.

The modeler shall select the following as allowed by their program:

- A time-step varying interior surface convection heat transfer algorithm, or constant surface convection coefficient(s) applied to each conduction path interior surface face

  - For tested programs with multiple options for time-step varying interior surface convection algorithms, the user shall select the most appropriate algorithm based on the test cell geometry and construction and the heating system fan supply airflow rate provided in the accompanying file ET100B-Measurements-GMT+1.csv (see Section 2.2.6.3.1 [Case ET100B1])

- A time-step varying interior surface infrared radiation exchange algorithm.

  - For tested programs with multiple options for time-step varying radiation exchange algorithms, the user shall select the most appropriate algorithm based on the test cell geometry and construction.

The modeler shall indicate the applied algorithms or values in Item S2 of their pro-forma modeler report; see ModRep_Proforma_ET100series(mmddyy).docx included with the accompanying electronic media.

Informative notes:

- This replaces the constant interior combined convective and radiative surface heat transfer coefficients specified for Case ET100B1

- Fan supply airflow rate varies hourly around an average of approximately 21.5 ACH for the best steady-state data period of this test case

- During pre-trial sensitivity tests, the spec authors observed a substantial difference between model results for buoyancy-driven versus mechanically driven interior surface heat transfer algorithms

- Constant convection-only coefficients are not provided in this test specification

- The exterior surface coefficients remain the same as in Case ET100B1.

2.2.8.4.2 Interior surface Texture

For programs that allow variation of interior surface convection with surface texture, interior surface texture shall be selected per instructions of Section 2.2.7.4.2 (Case ET100A3).

2.3 References

ANSI/ASHRAE (2020). Standard 140-2020. Method of Test for Evaluating Building Performance Simulation Software.  Atlanta, GA: American Society of Heating, Refrigerating, and Air-Conditioning Engineers.

Appendix C (2023). Appendix C (draft) of this test specification is included with the “SupplementaryFiles” folder within the accompanying electronic media.

ASHRAE 2021 Handbook of Fundamentals.  (2021).  Atlanta, GA: American Society of Heating, Refrigerating, and Air-Conditioning Engineers.

ASHRAE 2005 Handbook of Fundamentals.  (2005).  Atlanta, GA: American Society of Heating, Refrigerating, and Air-Conditioning Engineers.

ASHRAE 2021 Handbook of Fundamentals.  (2021a).  Atlanta, GA: American Society of Heating, Refrigerating, and Air-Conditioning Engineers. See pp. 26.7, 26.14, 26.15. Cites the following:

- Robinson, H.E.  and F.J. Powlitch. (1954). The thermal insulating value of airspaces. National Bureau of Standards (now National Institute of Standards and Technology). NBS Report 3030.

- Robinson, H.E., F.J. Powell, and L.A. Cosgrove. (1957). Thermal resistance of airspaces and fibrous insulations bounded by reflective surfaces. National Bureau of Standards (now National Institute of Standards and Technology). Building Materials and Structures Report 151.

EnergyPlus Weather File (EPW) Data Dictionary. (2022). http://climate.onebuilding.org/papers/EnergyPlus_Weather_File_Format.pdf

P. Girault and G. Guyon. (1999). "Configuration Physique et Geometrique des Cellules ETNA", Electricité de France, Moret sur Loing, France. 1999.Aout 99.

Neymark, J., Girault, P., Guyon, G., Judkoff, R., LeBerre, R., Ojalvo, J., Reimer, P. (2004). ETNA BESTEST Empirical Validation Test Specification. Golden, Colorado, US: J. Neymark & Associates; Moret sur Loing, France: Electricité de France. This document is available upon request; contact Joel Neymark (neymarkj@msn.com).

[Intentionally blank to not lose format of above]