## A
Std140_CE_a_Output.xls
Output spreadsheet for HVAC BESTEST Cases CE100 through CE200
INSTRUCTIONS
1. Use specified units
2. Data entry is restricted to columns B through T and rows 25 through 38. The protection
option has been employed to help assure that data is input in the correct cells.
3. February totals are consumption and or loads just for the month of February. Similarly,
February means, maxima, and minima are those values just for the month of February.
4. Cooling Energy Consumption, Evaporator Coil Load, Zone Load, and COP (Coefficient
of Performance) are defined in the Glossary appendix.
[5 empty] | F e b r u a r y T o t a l s | [6 empty] | February Mean |  | February Maximum |  |  | February Minimum
|  | Cooling Energy Consumption |  |  | Evaporator Coil Load |  |  |  | Zone Load
|  |  | Supply | Condenser | [8 empty] | Humidity |  |  | Humidity |  |  | Humidity
Cases | Total | Compressor | Fan | Fan | Total | Sensible | Latent | Total | Sensible | Latent | COP | IDB | Ratio | COP | IDB | Ratio | COP | IDB | Ratio
| (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) |  | (°C) | (kg/kg) |  | (°C) | (kg/kg) |  | (°C) | (kg/kg)
CE100 | 508.102 | 508.102 | 0 | 0 | 3703.39 | 3703.39 | 0 | 3703.39 | 3703.39 | 0 | 7.2887 | 72 | 0.0050379 | 7.2895 | 72 | 0.0050379 | 7.2878 | 72 | 0.0050379
CE110 | 508.102 | 508.102 | 0 | 0 | 3703.39 | 3703.39 | 0 | 3703.39 | 3703.39 | 0 | 7.2887 | 72 | 0.0050379 | 7.2895 | 72 | 0.0050379 | 7.2878 | 72 | 0.0050379
CE120 | 513.845 | 513.845 | 0 | 0 | 3703.15 | 3703.15 | 0 | 3703.15 | 3703.15 | 0 | 7.2068 | 80 | 0.0058465 | 7.2076 | 80 | 0.0058465 | 7.2059 | 80 | 0.0058465
CE130 | 28.4966 | 28.4966 | 0 | 0 | 173.472 | 173.472 | 0 | 173.472 | 173.472 | 0 | 6.0875 | 72 | 0.0050379 | 6.0883 | 72 | 0.0050379 | 6.0866 | 72 | 0.0050379
CE140 | 28.4966 | 28.4966 | 0 | 0 | 173.472 | 173.472 | 0 | 173.472 | 173.472 | 0 | 6.0875 | 72 | 0.0050379 | 6.0883 | 72 | 0.0050379 | 6.0866 | 72 | 0.0050379
CE150 | 599.413 | 599.413 | 0 | 0 | 4492.25 | 3753.05 | 739.2 | 4492.25 | 3753.05 | 739.2 | 6.2612 | 72 | 0.0072527 | 6.2627 | 72 | 0.007254 | 6.2598 | 72 | 0.0072514
CE160 | 599.143 | 599.143 | 0 | 0 | 4492.8 | 3753.6 | 739.2 | 4492.8 | 3753.6 | 739.2 | 6.265 | 80 | 0.0083872 | 6.2663 | 80 | 0.0083887 | 6.2637 | 80 | 0.0083857
CE165 | 599.143 | 599.143 | 0 | 0 | 4492.8 | 3753.6 | 739.2 | 4492.8 | 3753.6 | 739.2 | 6.265 | 80 | 0.0083872 | 6.2663 | 80 | 0.0083887 | 6.2637 | 80 | 0.0083857
CE170 | 329.761 | 329.761 | 0 | 0 | 2219.06 | 1479.86 | 739.2 | 2219.06 | 1479.86 | 739.2 | 4.4877 | 72 | 0.0098179 | 4.4905 | 72 | 0.0098239 | 4.4849 | 72 | 0.0098119
CE180 | 532.09 | 532.09 | 0 | 0 | 4555.11 | 1598.31 | 2956.8 | 4555.11 | 1598.31 | 2956.8 | 3.0038 | 72 | 0.015932 | 3.0063 | 72 | 0.015941 | 3.0015 | 72 | 0.015924
CE185 | 532.09 | 532.09 | 0 | 0 | 4555.11 | 1598.31 | 2956.8 | 4555.11 | 1598.31 | 2956.8 | 3.0038 | 72 | 0.015932 | 3.0063 | 72 | 0.015941 | 3.0015 | 72 | 0.015924
CE190 | 77.4414 | 77.4414 | 0 | 0 | 563.692 | 194.092 | 369.6 | 563.692 | 194.092 | 369.6 | 2.5062 | 72 | 0.01609 | 2.5201 | 72 | 0.016158 | 2.4928 | 72 | 0.01602
CE195 | 77.4414 | 77.4414 | 0 | 0 | 563.692 | 194.092 | 369.6 | 563.692 | 194.092 | 369.6 | 2.5062 | 72 | 0.01609 | 2.5201 | 72 | 0.016158 | 2.4928 | 72 | 0.01602
CE200 | 705.871 | 705.871 | 0 | 0 | 5500.52 | 4279.5 | 1221.02 | 5500.52 | 4279.5 | 1221.02 | 6.0627 | 72 | 0.0080745 | 6.0642 | 72 | 0.0080759 | 6.0613 | 72 | 0.008073